## Weekly
FM
PM Schedule | PM Schedule Description | Task Plan
W-BAG-01-02 | WEEKLY BARRIER ARM GATES INSPECTION | BAG-W-01
W-EG-01-02 | WEEKLY BOILER INSPECTION | HB-05
W-HB-01-02 | WEEKLY BUILDING MAINTENANCE ROUNDS | ROUNDS-W-02
W-PW-01-02 | WEEKLY BULK WATER STATION ROUNDS | BWS-W-01
W-ROUNDS-01-02 | WEEKLY EMERGENCY GENERATOR INSPECTION | EG-05
W-ROUNDS-02-02 | WEEKLY MECHANICAL ROUNDS | ROUNDS-01
W-ROUNDSBWS-02-02 | WEEKLY WASHBAY INSPECTION | PW-W-01
W-WS-01-02 | WEEKLY WATER SOFTENER INSPECTION | WS-01
FI
PM Schedule | PM Schedule Description | Task Plan
BUILDING CHECKS | EMERGENCY OPERATIONS CENTRE DAILY AIR HANDLING RM CHECKS
EOC-ACU-W | EMERGENCY OPERATIONS CENTRE WEEKLY LIEBERT ACU - SERVING RADIO ROOM | FI-AC-01
EOC-AH-RM-D | EMERGENCY OPERATIONS CENTRE DAILY AIR HANDLING RM CHECKS | FI-AHU-02
EOC-AHU-W | EMERGENCY OPERATIONS CENTRE WEEKLY LIEBERT AHU - DATA CENTRE ROOM INSPECTIONS | FI-AHU-02
EOC-BOILER-RM-D | EMERGENCY OPERATIONS CENTRE DAILY BOILER RM CHECKS | FI-HB-02
EOC-CHILLER-RM-D | EMERGENCY OPERATIONS CENTRE DAILY CHILLER RM CHECKS | FI-CH-02
EOC-LEVEL-(-2)-D | EMERGENCY OPERATIONS CENTRE DAILY LEVEL -2 CHECKS | FI-EOC-MECH-01
EOC-LEVEL-0-(-1)-D | EMERGENCY OPERATIONS CENTRE DAILY CHECKS LEVEL 0 & -1 | FI-EOC-MECH-02
EOC-LEVEL-0-WEST-D | EMERGENCY OPERATIONS CENTRE DAILY LEVEL 0 WEST CHECKS | FI-EOC-MECH-03
LAN-BW | SNOW CLEARING - MONTHLY CONTRACT AREAS
SNOW-REMOVAL | WEEKLY BOILER INSPECTION | HB-05
W-HB-01-02 | WEEKLY MECHANICAL ROUNDS | ROUNDS-01
W-ROUNDS-01-02 | WEEKLY VACANT PROPERTIES MECHANICAL & PLUMBING CHECK

## FA-A-01F
FA-A-01F | Annual Fire Alarm Inspection (Full Checklist)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CAN/ULC-S536 & 537, Standards for inspection and testing for FA systems
30 | ***CONTROL UNIT OR TRANSPONDER TEST***
31 | Power "ON" visual indicator operates
32 | Common visual trouble signal operates
33 | Common audible trouble signal operates
34 | Trouble signal silence switch operates
35 | Main power supply failure trouble signal operates
36 | Ground fault tested for positive and negative indication initiates trouble signal
37 | Alert signal operates
38 | Alarm signal operates
39 | Automatic transfer from alert signal to alarm signal operates. Time: _________
40 | Manual transfer from alert signal to alarm signal operates
41 | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on a two-stage system
42 | Alarm signal silence inhibit function operates
43 | Alarm signal manual silence operates
44 | Alarm signal silence visual indication operates
45 | Alarm signal and visible signal devices, when silenced, automatically reinitiate upon subsequent alarm
46 | Alarm signal silence automatic cut-out timer
47 | Audible and visual alarm signals programmed and operate per design and specification
48 | Input circuit, alarm and supervisory operation, including audible and visual indicator operates
49 | Input circuit supervision fault caused a trouble indication
50 | Output circuit alarm indicator operates
51 | Output circuit supervision faulty causes a trouble indication
52 | Visible indicate test (Lamp test) operates
53 | Code signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter
54 | Code signal sequences operate are not interrupted by subsequent alarms
55 | Ancillary device control circuit is rated for the intended purpose
56 | Ancillary device by-pass results in trouble signal
57 | Input circuit to output circuit operation, including ancillary device circuits for correct program operation, as per design and specification
58 | Fire alarm system reset operates
59 | Smoke detectors alarm verification (status change confirmation)
60 | **VOICE COMMUNICATE TEST***
61 | Power "ON" indicator operates
62 | Common visual trouble signal operates
63 | Common audible trouble signal operates
64 | Trouble signal silence switch operates
65 | All-call voice paging, including visual indicator, operates
66 | Output circuits for selective voice paging, including visual indication, operates
67 | Output circuits for selective voice paging trouble operation, including visual indication, operates
68 | Microphone, including press to talk switch, operates
69 | Operation of voice paging does not interfere with initial inhibit time of alert or alarm signal
70 | All-call voice paging operates (on emergency power supply)
71 | Upon failure of one amplifier, system automatically transfer to backup amplifier
72 | Circuits for emergency telephone call-in operation, including audible and visual indication operates
73 | Circuit for emergency telephone for operation, including 2-way voice communication, operates
74 | Circuits for emergency telephone trouble operation, including visual indication, operates
75 | Emergency telephone verbal communication operates
76 | Emergency telephone operable or in-use tone at handset operates
77 | Test voice communication busses in standby mode
78 | ***CONTROL UNIT OR TRANSPONDER INSPECTION***
79 | Control unit or transponder location:
80 | Control unit or transponder identification:
81 | Input circuit designations correctly identified in relation to connected field devices
82 | Output circuit designations correctly identified in relation to connected field devices
83 | Correct designations for common control functions and indicators
84 | Plug-in components and modules securely in place
85 | Plug-in cables securely in place'
86 | Record the date, revision and version of firmware and software program
87 | Clean and free of dust and dirt
88 | Fuses in accordance with manufacturer's specification
89 | Control unit or transponder lock functional
90 | Termination points from wiring to field device secure
91 | ***POWER SUPPLY INSPECTION***
92 | Control unit or transponder location:
93 | Control unit or transponder identification:
94 | Fuses in accordance with manufacturer's specification
95 | Adequate to meet the requirement of the system
96 | ***EMERGENCY POWER SUPPLY TEST AND INSPECTION***
97 | Control unit or transponder location:
98 | Control unit or transponder identification:
99 | Correct battery type as recommended by manufacturer
100 | Correct battery rating as determined by battery calculations based on full system load
101 | Battery voltage with main power supply "ON"
102 | Battery voltage and current with main power supply "OFF" and fire alarm system in supervisory condition
103 | Voltage: ________V dc
104 | Current: ________A dc
105 | Battery voltage and current with main power supply "OFF" and fire alarm system in full load condition
106 | Voltage: ________V dc
107 | Current: ________A dc
108 | Charging current on a fully charged battery
109 | Inspected for physical damage
110 | Terminals cleaned and lubricated
111 | Terminal clamped tightly
112 | Specific gravity of the electrolyte is within manufacturer's specification
113 | Electrolyte leakage
114 | Adequately ventilated
115 | Record manufacturer's date code or in-service date
116 | Disconnection causes trouble signal
117 | Indicate type of battery test performed on a fully charged battery
118 | i) Required supervisory load for 24h followed by the required full load operation; or
119 | ii) A silent test by using the load resistor method may be used for the full duration test; or
120 | iii) Silent accelerated test; or
121 | iv) A battery capacity meter test; or
122 | v) In lieu of the above battery tests, replace the battery with a new set having a current date code, amp-hour capacity and type
123 | Record calculated battery capacity
124 | Record battery terminal voltage after completion of tests
125 | Battery voltage not less than 85% of its rating after the tests
126 | Generator provides power to the AC circuit serving the fire alarm system
127 | Trouble condition at the generator results in an audible common trouble signal and a visual indication at the require annunciator
128 | ***ANNUNCIATOR, REMOTE TROUBLE SINGAL UNIT TEST AND INSPECTION***
129 | Annunciator or sequential display location:
130 | Annunciator or sequential display identification:
131 | Power "ON" indicator operates
132 | Individual alarm and supervisory input zone clearly indicated and separately designated
133 | Individual alarm and supervisory input zone designation labels are properly identified
134 | Common trouble signal operates
135 | Visual indicator test (Lamp test) operates
136 | Input wiring from control unit or transponder is supervised
137 | Alarm signal silence visual indication operates
138 | Switches for ancillary functions operates as per design and specification
139 | Other ancillary function visual indicators operate
140 | Manual activation of alarm signal and indication operates
141 | Displays are visible in installed location operates
142 | Operates on emergency power
143 | ***ANNUNCIATORS OR SEQUENTIAL DISPLAYS***
144 | Annunciator or sequential display location:
145 | Annunciator or sequential display identification:
146 | Power "ON" indicator operates
147 | Individual alarm and supervisory zone indication operates
148 | Exception: Operation on each individual alarm and supervisory zone indication
149 | Specify method of confirmation
150 | Minimum of one alarm zone and one supervisory zone tested per annunciator or sequential display to confirm operation
151 | Individual alarm and supervisory zone designation labels are properly identified
152 | When field device utilized, device labels confirmed to correpond with actual field location
153 | Common trouble signal operates
154 | Visual indicator test (Lamp test) operates
155 | Input wiring from control unit or transponder is supervised
156 | Alarm signal silence visual indication operates
157 | Switches for ancillary functions operates as per design and specification
158 | Other ancillary function visual indicators operate
159 | Manual activation of alarm signal and indication operates
160 | Displays are visible in installed location operates
161 | ***REMOTE TROUBLE SIGNAL UNIT TEST AND INSPECTION***
162 | Remote trouble signal unit location:
163 | Remote trouble signal unit identification:
164 | Input wiring from control unit or transponder is supervised
165 | Visual trouble signal operates
166 | Audible trouble signal operates
167 | Audible trouble signal silence operates
168 | ***PRINTER TEST***
169 | Operates as per design and specification
170 | Zone of each alarm initiating device is correctly printed
171 | Rated voltage is present
172 | ***OPERATION TEST FOR DATA COMMUNICATION LINK TEST***
173 | Control unit or transponder location:
174 | Control unit or transponder identification:
175 | Data communication link identification:
176 | Confirm that a trouble signal is received under open loop fault
177 | Fault isolation modules are installed in Data communication link serving Field devices
178 | Fault isolation in Data communication link is provided between control unit and transponders
179 | ***INTERCONNECTION TO THE FIRE SIGNAL RECEIVING CENTRE
180 | The fire signal receiving centre transmitting is integral to the fire alarm control unit
181 | An interconnection between the fire alarm control unit and a separate fire signal receiving centre transmitted is provided
182 | Where an interconnection between the fire alarm control unit and a separate fire signal receiving centre transmitter is provided with a demarcation terminal box
183 | The demarcation terminal box is located in the same room as the fire alarm control unit is connected to
184 | The demarcation terminal box is labeled "Fire Alarm Demarcation"
185 | Test and confirmed operation of fire relay
186 | Test and confirmed operation of trouble relay
187 | Test and confirmed operation of supervisory relay
188 | Confirm that the fire alarm transmission to the fire signal receiving centre is received
189 | Confirm that the supervisory transmission to the fire signal receiving centre is received
190 | Confirm that a trouble transmission to the fire signal receiving centre is received
191 | Operation of the fire alarm receiving centre transmitter bypass means results in trouble indication at the control unit
192 | Operation of the fire signal receiving centre transmitter bypass means transmits a trouble signal to the fire signal receiving centre
193 | Record the name and the telephone number of the fire signal receiving centre
194 | ***ANCILLARY DEVICE CIRCUIT TEST***
195 | Record specific type of ancillary circuit
196 | ***DEFICIENCIES, RECOMMENDATION & REMARKS***
197 | Mention any defects and rectification work if required
198 | ***FIELD DEVICE RECORD***
199 | List out all individual field device with testing record
200 | Findings Reported To Maintenance Supervisor
201 | Above task plan is the minimum requirement to follow
202 | Contractor is responsible to comply with all update and applicable codes as required.
Existing tasks in EAM
Sequence | Description
10 | Fire Alarm System Tested Pass Fail
20 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
30 | Pre Job Hazard Assessment Completed?

## Quarterly
PM SCHEDULE | PM SCHEDULE DESCRIPTION | TASK PLAN | ORGANIZATION
Q-FSS-01-02 | QUARTERLY FIRE SPRINKLER INSPECTION | FSS-04 | COC
Q-AED-01-02 | QUARTERLY AUTOMATED EXTERNAL DEFIBRILLATOR | AED-01 | COC
Q-FC-01-02 | QUARTERLY FAN COIL UNIT INSPECTION | FC-Q-01 | COC
Q-WT-LEG-01-03 | QUARTERLY LEGIONELLA TEST | WT-LEG-01 | COC
Q-AHU-01-02 | QUARTERLY AIR HANDLING UNIT INSPECTION | AHU-Q-01 | COC
Q-FN-01-02 | QUARTERLY FURNACE INSPECTION | FN-04 | COC
Q-CP-01-03 | QUARTERLY AIR COMPRESSOR INSPECTION | CP-Q-01 | COC
Q-SAFETY-01-02 | QUARTERLY WORKPLACE SAFETY INSPECTION (Mechanical and Electrical Room) | W-Q-01 | COC
Q-SP-01-02 | QUARTERLY SOLAR PANEL CLEANING & INSPECTION | SP-01 | COC
EOC-ACU-Q | (Deactiv) EMERGENCY OPERATIONS CENTRE QUARTERLY LIEBERT ACU - SERVING RADIO ROOM |  | FI
EOC-CT-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY FLUID COOLER INSPECTIONS |  | FI
EOC-ET-Q | (Deactivated) EMERGENCY OPERATIONS CENTRE QUARTERLY EXPANSION TANK INSPECTIONS |  | FI
EOC-F-Q | (deactivated) EMERGENCY OPERATIONS CENTRE QUARTERLY FAN INSPECTIONS |  | FI
EOC-FCU-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY FAN COIL UNIT INSPECTIONS |  | FI
EOC-HE-Q | (deactivated) EMERGENCY OPERATIONS CENTRE QUARTERLY CABINET HEATER INSPECTIONS |  | FI
EOC-HRU-Q | (Deactivate)EMERGENCY OPERATIONS CENTRE QUARTERLY HEAT RECOVERY UNIT INSPECTIONS |  | FI
EOC-MANHOLE-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY CHECK ENMAX MANHOLE FOR WATER LEVEL |  | FI
EOC-ROOF-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY ROOF CLEANING |  | FI
EOC-SIDE-STREAM-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY SIDE STREAM FILTER REPLACEMENT |  | FI
EOC-WS-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY WATER SOFTENER INSPECTIONS |  | FI
FILTER | QUARTERLY FILTER INSPECTION/REPLACEMENT |  | FI
GREASE-Q | QUARTERLY GREASE TRAP CLEAN-OUT |  | FI
Q-WTR-CHEM-01-01 | QUARTERLY WATER TREATMENT CLOSED LOOP HEATING SYSTEM |  | FI
Q-WTR-CHEM-01-02 | QUARTERLY WATER TREATMENT CLOSED LOOP HEATING SYSTEM |  | FI
EOC-ROOF-Q | EMERGENCY OPERATIONS CENTRE QUARTERLY ROOF CLEANING |  | FI
SUMP-33 | SUMP PUMP CLEAN-OUT SANITARY SUMPS |  | FI
FILTER | QUARTERLY FILTER INSPECTION/REPLACEMENT |  | FI
SUMP | SUMP CLEAN OUT (4 MONTHS) |  | FI

## LS-EWS-A
LS-EWS | ANNUAL EYE WASH STATION INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Ensure eyewash station is properly mounted
30 | Ensure sterile bottles are in place
40 | Check expiration of eye wash sterile, replace as needed
50 | Located within 10 seconds' travel distance from a hazard.
60 | Findings reported to Maintenance Supervisor

## EWS-M-01
EWS-M-01 | MONTHLY EYE WASH STATION INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Water supply delivers required flow (1.5L /min) for 15 mins (ANSI Z358.1)
30 | Check water temperature is warm and within 15.6 to 37.8 Deg.C (ANSI Z358.1)
40 | Verify the eye wash fixtures and accessories is functional
50 | Findings reported to Maintenance Supervisor

## EWSS-A-01
EWSS-A-01 | ANNUAL EMERGENCY EYEWASH STATION & SHOWER INSPECTION
Sequence | Description | Type
10 | Pre Job Hazard Assessment completed? | Question (Yes/No)
20 | As per Code ANSI Z358.1-2014 Emergency Eyewash & Shower Equipment fo inspection | Checklist Item
30 | For Eye Wash Stations: | Checklist Item
40 | The eyewash safety station delivers at least 0.4 gallons (1.5L per minute) of water per minute for 15 minutes (Sections 5.1.6, 5.4.5). | Checklist Item | W
50 | Water delivered by eyewash shall be tepid (60-100°F or 15.6 to 37.8 Deg.C). (Section 5.4.6; B6) | Checklist Item | W
60 | Verify the eye wash fixtures and accessories is functional | Checklist Item | W
70 | Identification: The area around the eyewash station must be well-lit and the unit must include a highly visible sign (Section 5.4.3). | Checklist Item
80 | The safety station washes both eyes simultaneously and the water flow allows the user to hold the eyes open without exceeding 8” above the spray heads (Section 5.1.8). | Checklist Item
90 | Spray heads are protected from airborne contaminants. Covers are removed by the water flow (Section 5.1.3). | Checklist Item | W
100 | Water flow pattern is 33-53” from the floor and at least 6” from a wall or nearest obstruction (Section 5.4.4). | Checklist Item
110 | Hands-free stay-open valve activates in one second or less (Sections 5.1.4, 5.2). | Checklist Item
120 | Controlled, low velocity flow rinses both eyes and is not injurious to user. (Section 5.1.1) | Checklist Item
130 | Water flow is sufficiently high to allow user to hold eyes open while rinsing. (Section 5.1.7) | Checklist Item | W
140 | Valve actuator is easy to locate and readily accessible to user. (Section 5.2) | Checklist Item
150 | Eyewash unit within 10 seconds (approximately 55 feet) of hazard, on the same level as hazard and with unobstructed travel path. | Checklist Item
160 | Where strong acids or caustics are being handled, emergency eyewash unit should be located adjacent to the hazard, | Checklist Item
170 | An appropriate professional should be consulted for advice on the proper distance. (Section 5.4.2; B5) | Checklist Item
180 | Training: Instruct all employees in the location and proper use of eyewash units. (Section 5.5.4) | Checklist Item
190 | For Combination of Emergency Eyewash Station and Shower (If applicable) | Checklist Item
200 | Water supply delivers required flow when shower and eye or eye/face wash are operated simultaneously. (Section 4.5.5, 7.4.4) | Checklist Item | W
210 | Hands-free stay-open valve activates in one second or less. (Section 4.2) | Checklist Item
220 | Height of water column is between 82” (208.3 cm) and 96” (243.8 cm) above the floor. (Section 4.1.3, 4.5.4) | Checklist Item
230 | Shower delivers 20 gallons (75.7 liters) of water per minute for 15 minutes in the required pattern. (Section 4.1.2, 4.5.5) | Checklist Item | W
240 | Water delivered by eyewash shall be tepid (60-100°F or 15.6 to 37.8 Deg.C). (Section 7.4.5; B6) | Checklist Item | W
250 | Verify the eye wash fixtures and accessories is functional | Checklist Item | W
260 | Identify Combination Unit location with highly visible sign. Area around the unit shall be well-lit. (Section 7.4.3) | Covered in 60
270 | Easily located, accessible actuator is no more than 69” (173.3 cm) above floor. (Section 4.2) | Checklist Item
280 | Center of the water pattern is at least 16” (40.6 cm) from any obstruction. (Section 4.1.4, 4.5.4) | Checklist Item
290 | At 60” (152.4 cm) above the floor, the water pattern is at least 20” (50.8 cm) in diameter. (Section 4.1.4) | Checklist Item
300 | Spray heads are protected from airborne contaminants. Covers are removed by water flow. (Section 5.1.3, 6.1.3) | Checklist Item | W
310 | Unit delivers at least 3.0 GPM (11.4 liters) (for eye/face wash) or 0.4 GPM (1.5 liters) (for eyewash) for 15 minutes. (Section 5.1.6, 6.1.6, 6.4.5) | Checklist Item
320 | Hands-free stay-open valve activates in one second or less. (Section 5.2, 6.1.4, 6.2) | Checklist Item
330 | Valve actuator is easy to locate and readily accessible to user. (Section 5.2, 6.2) | Checklist Item
340 | Combination unit within 10 seconds (approximately 55 feet) of hazard, on the same level as hazard and with unobstructed travel path. | Checklist Item
350 | Where strong acids or caustics are being handled, emergency eyewash unit should be located adjacent to the hazard, | Checklist Item
360 | An appropriate professional should be consulted for advice on the proper distance. (Section 7.4.2; B5) | Checklist Item
370 | Training: Instruct all employees in the location and proper use of eyewash units. (Section 7.5.4) | Checklist Item
380 | Findings Reported to Maintennace Supevisor | Question (Yes/No)
390 | Site evaluation to assure continued compliance to ANSI/ISEA Z358.1-2014. (if app) | Checklist Item
Remarks: | Annual PM should be carried out by the vendor or qualified professional trade (e.g. Plumber)

## EWSS-W-01
EWSS-W-01 | WEEKLY EMERGENCY EYEWASH STATION & SHOWER INSPECTION
Sequence | Description | Type
10 | Pre Job Hazard Assessment completed? | Question (Yes/No)
20 | As per Code ANSI Z358.1-2014 Emergency Eyewash & Shower Equipment for weekly activation | Checklist Item
30 | For Eye Wash Stations: | Checklist Item
30 | The eyewash safety station delivers at least 0.4 gallons of water per minute for 15 minutes (Sections 5.1.6, 5.4.5). | Checklist Item
40 | Water delivered by eyewash shall be tepid (60-100°F or 15.6 to 37.8 Deg.C). (Section 5.4.6; B6) | Checklist Item
50 | Verify the eye wash fixtures and accessories is functional | Checklist Item
70 | For Combination of Emergency Eyewash Station and Shower (If applicable) | Checklist Item
80 | Water supply delivers required flow when shower and eye or eye/face wash are operated simultaneously. (Section 4.5.5, 7.4.4) | Checklist Item
90 | Shower delivers 20 gallons (75.7 liters) of water per minute for 15 minutes in the required pattern. (Section 4.1.2, 4.5.5) | Checklist Item
100 | Water delivered by combination unit shall be tepid (60-100°F or 15.6 to 37.8 Deg.C). (Section 7.4.5; B6) | Checklist Item
110 | Verify the eye wash fixtures and accessories is functional | Checklist Item
120 | Spray heads are protected from airborne contaminants. Covers are removed by water flow. (Section 5.1.3, 6.1.3) | Checklist Item
130 | Findings Reported to Maintennace Supevisor | Question (Yes/No)
Remarks: | Verify and activate by in-house (i.e. building maintenance)

## ROUNDS-M-02
ROUNDS-M-02 | MONTHLY BUILDING MAINTENANCE ROUNDS
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | *****LIGHTS INSPECTION*****
20 | Do a light sweep of the area and replace burnt lights if needed
30 | *****PERIMETER INSPECTION*****
40 | Check curbs & sidewalks for (summer: debris, damages)
50 | Check curbs & sidewalks for (winter: snow, ice and damages)
60 | Garbage pick-up on all entrances
70 | Check for broken windows
80 | Check for vandalism/graffiti
90 | General condition assessment of the landscaped area (Irrigation, broken branches
100 | *****DOORS AND OPENINGS*****
110 | Check door operation and weather stripping,
120 | *****WASHROOM INSPECTION*****
130 | Check taps & aerators
140 | Check flush-o-meter
150 | Check for proper drainage of sinks, urinals & toilets
160 | Check bathroom partition and associated hardware (locks and hinges i.e.)
170 | Check air fresheners in applicable w/r-change batteries and cannister as req
180 | *****KITCHEN INSPECTION*****
190 | Check tap & aerator
200 | Check countertops for cracks & lifting
200 | *****WATER SOFTENER*****
210 | Ensure there is sufficient salt supply and does not exceed the max water level
220 | Ensure salt is not bridging by using the long handle tools
230 | Findings Reported To Maintenance Supervisor

## SAFETY-W-Q-01
SAFETY-W-Q-01 | QUARTERLY WORKPLACE SAFETY INSPECTION (Mechanical and Electrical Room)
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Conduct a safety inspection of the Office /Administration Area
20 | Fill-out and submit a Workplace Inspection - Office /Administration form X-515
30 | Findings reported to Maintenance Supervisor

## ROUNDS-M-01
ROUNDS-M-01 | MONTHLY MECHNICAL ROUNDS
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Daily visual check of Mechanical Rooms and Systems
20 | Record any readings or problems and log it in the round sheet
30 | Check systems on BMS, if applicable
40 | Check and inspect all filters for HVAC equipment
50 | Clean or replace filters for HVAC equipment as needed
60 | Spring: Shut down the Infrared heater
70 | Fall: Turn on the Infrared heater and check the thermostat if applicable
80 | *****WATER SOFTENER*****(If applicable)
90 | Ensure there is sufficient salt supply and does not exceed the max water level
100 | Ensure salt is not bridging by using the long handle tools
110 | Carry out water test to check hardness level
120 | Findings Reported To Maintenance Supervisor
120 | *******CHLORINE CHECK [Ralph Klein Park Comfort Station]*******
130 | Check of sodium hypochlorite levels (12%). Order more as required
140 | *****NEDERMAN DIESEL EMISSION EXHAUST*****(Fire Bldgs only)
150 | Check the fixing of the rail bracket
160 | Check the condition of hose
170 | Check the end stops
180 | Check the trolley stop
190 | Check the wheels of the suction trolley
200 | Check the suction trolley moves easy in the whole length of rail
210 | Check the guide way of the suction trolley regarding wears
220 | Clean the guide ways if necessary
230 | Check the rubber buffer and the shock absorber of suction trolley
240 | Check the nozzle condition
250 | Check enough suction power in the exhaust hose
260 | Check operation of balancer, ensure the hose lifts up properly
270 | Adjust lifting power of balancer if necessary
280 | Check the cord of the balancer
290 | Check the disconnection operation and clean the magnet if necessary
300 | Apply anti-oxidant joint compound to magnet for proper connection
310 | Check the tightness of the screws in the joint connectors of nozzle
320 | Check proper operation of exhaust fan
330 | Findings Reported To Maintenance Supervisor

## MECH-DH-S
MECH-DH | ANNUALLY CARBON MONOXIDE DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check ultraviolet lamp if applicable. Clean or replace as needed
30 | Check for proper fluid flow and for fluid leaks. Clean, adjust and repair as needed
40 | Measure relative humidity and adjust system as needed
50 | Check for system traps, pumps and control. Clean or replace as needed
60 | Check for fouling, corrosion, or degradation. Clean or replace as needed
70 | Check and clean strainers
80 | Visually inspect distributors, nozzles, drain pans for accumulation of biological growth
90 | Clean or disinfect as needed
100 | Findings Reported To Maintenance Supervisor

## FN-Q-01
FN-Q-01 | QUARTERLY FURNACE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Vacuum Unit (Including Blower And Burner Compartment) Thoroughly.
30 | Check Unit Access Panels’ Fastening And Access Panel Gasket For Damage.
40 | Turn Blower Wheel By Hand To Ensure It Rotates Freely.
50 | Check Firing Condition Observe Flame Record The Applicable Colour: Blue/Yellow
60 | If The Burner Has Been Burning Yellow, Then Clean Burner Chamber With Wire Brush
70 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage.
80 | Visually Inspect Heat Exchanger. Record Observations.
90 | Check Filters, change as required
100 | Findings Reported to Maintenance Supervisor
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Vacuum Unit (Including Blower And Burner Compartment) Thoroughly.
20 | Check Unit Access Panels’ Fastening And Access Panel Gasket For Damage.
30 | Replace Gasket If Damaged.
40 | Replace Belt If Needed.
50 | Turn Blower Wheel By Hand To Ensure It Rotates Freely.
60 | Lubricate As Per Manufacturer’S Recommendations.
70 | Swing Unit Back Into Place And Secure Latches.
80 | Check Firing Condition Observe Flame Record The Applicable Colour: Blue/Yellow
90 | If The Burner Has Been Burning Yellow, Then Clean Burner Chamber With Wire Brush
100 | Measure Motor Amperage And Record Actual Amperage: Name Plate Data
110 | Measure Motor Amperage And Record Actual Amperage: Measured Data
120 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage.
130 | Visually Inspect Heat Exchanger. Record Observations.
140 | Install Access Covers And Ensure They Are Secure. Note Any Unusual Vibrations.
150 | Findings Reported To Facility Supervisor And Facility Operations Coordinator

## FN-S-01-R21
FN-S-01-R21 | SEMI-ANNUAL FURNACE INSPECTION (RFP)
Sequence | Description
10 | **COMMON TASKS**
20 | Complete Pre Job Hazard Assessment
30 | Perform pre-work CO and gas safety check
40 | Vacuum Unit (Including Blower and Burner Compartment)
50 | Check Unit Access Panels’ Fastening and Access Panel Gasket for Damage.
60 | Replace Belt
70 | Ensure blower wheel rotates freely
80 | Lubricate As Per Manufacturer’s Recommendations
90 | Perform electronic combustion analysis and make adjustments as needed
100 | Verify Motor Amperage is within nameplate range
110 | Inspect and clean condensate pans and drains
120 | Verify unit safety controls are functioning
130 | Inspect all filters including MERV 13, replace or clean as needed
140 | Perform post-work CO and gas safety check
150 | Findings Reported To City Representative
160 | **FALL HEATING INSPECTION**
170 | Clean Burner Chamber
180 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage
190 | Visually Inspect Heat Exchanger
200 | Check dampers as required
210 | Check neutralizing agents and condition of condensate drain lines (if app)
220 | Inspect draft inducer and ensure proper operation (if app)
230 | **SPRING COOLING INSPECTION**
240 | Check refrigerant charge and perform leak check
250 | Inspect and Clean condenser and evaporator coil
260 | Comb all damaged fins
270 | Check Compressor Oil Level and evidence of oil leaks (if app)
280 | Check Refrigerant Operating Temperature And Pressures (if app)
290 | Check Condenser Fans And Tighten Set Screws (if app)
300 | Verify motor amperages are within nameplate ranges

## FC-Q-01
FC-Q-01 | QUARTERLY FAN COIL INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check Coil Unit While Operating.
20 | Confirm Operation Of Cooling/Heating Valves As Required
30 | Check Coils And Piping For Leaks, Damage And Corrosion; Repair As Necessary.
40 | Replace Filters As Required.
50 | Check Operation After Repairs.
60 | Clean Area.
70 | Fill Out Maintenance Checklist And Report Deficiencies.
80 | Findings Reported To Maintenance Supervisor

## MECH-FN-A
MECH-FN-A | ANNUALLY FURNACE INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Vacuum Unit (Including Blower And Burner Compartment) Thoroughly.
20 | Check Unit Access Panels’ Fastening And Access Panel Gasket For Damage.
30 | Replace or clean filters.
40 | Replace Belt.
50 | Turn Blower Wheel By Hand To Ensure It Rotates Freely.
60 | Check fan blades and fan housing. Clean or replace as needed
70 | Lubricate As Per Manufacturer’S Recommendations.
80 | Swing Unit Back Into Place And Secure Latches.
90 | Check Firing Condition Observe Flame.Record Colour: Blue/Yellow
100 | If The Burner Has Been Burning Yellow, Then Clean Burner Chamber With Wire Brush
110 | Measure Motor Amperage And Record Actual Amperage: Name Plate Data
120 | Measure Motor Amperage And Record Actual Amperage: Measured Data
130 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage.
140 | Visually Inspect Heat Exchanger. Record Observations.
150 | Install Access Covers And Ensure They Are Secure. Note Any Unusual Vibrations.
160 | Check for proper damper operation. Clean or adjust as needed
170 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM
Sequence | Description
10 | Vacuum Unit (Including Blower And Burner Compartment) Thoroughly.
20 | Check Unit Access Panels’ Fastening And Access Panel Gasket For Damage.
30 | Replace Gasket If Damaged.
40 | Replace Belt.
50 | Turn Blower Wheel By Hand To Ensure It Rotates Freely.
60 | Lubricate As Per Manufacturer’S Recommendations.
70 | Swing Unit Back Into Place And Secure Latches.
80 | Check Firing Condition Observe Flame.Record Colour: Blue/Yellow
90 | If The Burner Has Been Burning Yellow, Then Clean Burner Chamber With Wire Brush
100 | Measure Motor Amperage And Record Actual Amperage: Name Plate Data
110 | Measure Motor Amperage And Record Actual Amperage: Measured Data
120 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage.
130 | Visually Inspect Heat Exchanger. Record Observations.
140 | Install Access Covers And Ensure They Are Secure. Note Any Unusual Vibrations.
150 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
160 | Pre Job Hazard Assessment Completed?

## FCU-A-01
FCU-A-01 | ANNUALLY FAN COIL UNIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check proper function of fan coil unit with thermostat
20 | Check and tighten all set screws, bolts, locking collars and sheaves
30 | Remove access panel and vaccum inside of unit and coils
40 | Check coils and piping for leaks, damage and corrosion as necessary
50 | Lubricate blower shaft and fan motor bearings, if necessary
60 | Clean the fan wheels. Remove any rust from the shaft
70 | Rotate the fan wheel and check for obstructions.
80 | Clean coil, air filter, drip pan, and drain line with water and solvent
90 | Clean or replace filters as required
100 | Inspect, clean, and tighten all electrical connections, control valve and wiring
110 | Examine insulation, flex connections for cracks or leaks. Repair if needed
120 | Fill out maintenance checklist and report deficiencies
130 | Findings Reported To Maintenance Supervisor

## HFE-W-01
HFE-W-01 | WEEKLY HYBRID FIRE EXTINGUISHER (VORTEX) INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & NFPA 770 Chapter 14 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required (if applicable)
60 | Inspect inert gas (e.g. Nitrogen) and water supply lines
70 | Review Annunciator Panel history (if applicable).
80 | Inspect emitters to ensure they are not obstructed
90 | Verify that emitter covers are still in place
100 | Fire Alarm Control panel is in "Normal" ready condition
110 | System isolation valves are locked in fully open position
120 | Findings Reported To Maintenance Supervisor

## HFE-S-01
HFE-S-01 | SEMI-ANNUAL HYBRID FIRE EXTINGUISHER (VORTEX) INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & NFPA 770 Chapter 14 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | Complete all steps outlined in the "Weekly Inspection" section
70 | Inspect the nitrogen tank pressure levels for low pressure. If low pressure
80 | condition exists, check for root cause and repair
90 | Recharge cylinders, as required. Where container pressure gauges are used for
100 | this purpose, readings shall be compared to a separate,
110 | calibrated device at least annually
120 | Inspect water storage tank level (if applicable) & fill or replace, as required
130 | Correct promptly any deficiency
140 | All inspection results shall be recorded in a report and
150 | on each cylinder record secured tag
160 | Findings Reported To Maintenance Supervisor

## HFE-A-01
HFE-A-01 | ANNUAL HYBRID FIRE EXTINGUISHER (VORTEX) INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & NFPA 770 Chapter 14 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | Complete all steps outlined in the "Weekly Inspection" and
70 | "Semi-Annual Inspection" sections
80 | Perform a functional test of the system (discharge test is not required)
90 | Check hybrid media containers for signs of damage
100 | Cycle the inert gas (e.g. Nitrogen) valves for proper
110 | operation (discharge test is not required)
120 | Replace water in storage containers
130 | Drain and inspect interior of water tank. Clean (flush) water
140 | tank to remove debris. Refill water tank
150 | Inspect all system hoses. If visual examination shows any damage or
160 | deterioration, the affected hoses shall be replaced immediately
170 | Check and test all time delays for operation
180 | Check and test all audible notification appliances for operation
190 | Check that all warning signs are installed and visible
200 | Check operation of all manual release devices
210 | Check and test each automatic detector using methods specified in NFPA 72
220 | Check and verify functional operation of system interlocks
230 | All inspection results shall be recorded in a report and
240 | on each cylinder record secured tag
250 | Findings Reported To Maintenance Supervisor

## HFE-QQ-01
HFE-QQ-01 | QUINQUENNIAL HYBRID FIRE EXTINGUISHER (VORTEX) INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & NFPA 770 Chapter 14 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | Inspections shall be conducted only by authorized personnel
70 | Complete all steps outlined in the "Annual Inspection" section
80 | Inert gas (e.g. Nitrogen) cylinders that are continuously in service without
90 | being discharged shall be given a complete external visual
100 | inspection a minimum of every 5 years
110 | Visual inspection shall be in accordance with Section 3 of CGA C-6, except that
120 | the cylinders do not need to be emptied or stamped while under pressure
130 | All hoses shall be tested or replaced a minimum of every 5 years
140 | ****Hydrostatic Tests****
150 | At a minimum of every 5 years, all system hoses shall be tested at 1.5 time the
160 | maximum container pressure at 130°F/54°C
170 | The testing procedure shall be conducted, as outlined below:
180 | - Remove the hose from any attachment
190 | - Place the hose assembly into a protective enclosure designed
200 | to permit visual observation of the test
210 | - Fill the hose completely with water prior to testing
220 | - Apply pressure at a rate-of-pressure rise to reach the test
230 | pressure within a minimum of 1 minute
240 | - Maintain test pressure for one full minute. Note any distortion or
250 | leakage that occurs during the test
260 | - If the test pressure has not dropped, or if the couplings have not
270 | moved, release pressure in the hose assembly
280 | - If no permanent distortion has occurred, the hose assembly has
290 | passed the hydrostatic test
300 | 5-Year inspection and test results shall be recorded in a report and
310 | on a tag permanently attached to each nitrogen cylinder
320 | Findings Reported To Maintenance Supervisor

## LS-FAK-S
LS-FAK-S | SEMI-ANNUALLY FIRST AID KIT INSPECTION
Sequence | Description
10 | Ensure the first aid kit is maintained in a clean, dry and servicable location
20 | First Aid Kit shall at least consist of followings:-
30 | 10 antiseptic cleansing towelettes, individually packaged;
40 | 25 sterile adhesive dressings, individually packaged;
50 | Ten 10 centimetres x 10 centimetres sterile gauze pads, individually packaged;
60 | Two 10 centimetres x 10 centimetres sterile compress dressings, with ties, individually packaged
70 | Two 15 centimetres x 15 centimetres sterile compress dressings, with ties, individually packaged;
80 | Two conform gauze bandages — 75 millimetres wide;
90 | 3 cotton triangular bandages;
100 | 5 safety pins — assorted sizes;
110 | 1 pair of scissors;
120 | 1 pair of tweezers;
130 | One 25 millimetres x 4.5 metres of adhesive tape;
140 | One crepe tension bandage — 75 millimetres wide;
150 | One resuscitation barrier device with a one-way valve;
160 | 4 pairs of disposable surgical gloves;
170 | One first aid instruction manual (condensed);
180 | One inventory of kit contents;
190 | One waterproof waste bag.
200 | Check expiry date and confirm sufficient supplies available in first aid kit

## BAG-S-01
BAG-S-01 | SEMI-ANNUALLY BARRIER ARM GATES INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Test bypass switch in the control panel for normal operation
30 | Check for any unusual movements e.g. sudden impact, slow actuation
40 | Check if the arm gate is tilted enough to avoid contact with passing vehicle
50 | Check for loose and improper wiring connections
60 | Check if holding time is enough to smoothly pass a vehicle
70 | Inspect for general conditions: no broken, damaged and loosed parts
80 | Inspect for unusual noise and binding during operation
90 | Check gate for mis-alignment.
100 | If possible, visually check linkages if needs lubrication
110 | Check for loose and improper wiring connections
120 | Findings Reported To Maintenance Supervisor

## SP-BR-A-01
SP-BR-A-01 | ANNUAL SOLAR PANEL BRACKET INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Take all precautions do not touch any part of the PV panels
30 | Workers must use proper PPE, insulated tools, ladders and/or handling equipment.
40 | Check for proper condition for mounting system of solar panel system
50 | Tighten any loosen bolts, nuts, screws for the mounting system if necessary
60 | Electrical conduits, cable tray and assocaited components are well protected
70 | Allowance for sufficient clearances between arrays to access for maintenance, inspections, drainage;
80 | Check and clear debris for the drainage on the roof to avoid ponding
90 | Provision of appropriate secure access to the roof;
100 | Provision of appropriate warning signage for maintenance workers;
110 | Findings Reported To Maintenance Supervisor

## NH3-CD-A-01
NH3-CD-A-01 | ANNUAL WATERLESS ADIABATIC COOLING SYSTEM SHUTDOWN
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Visually inspect cleanliness and stability
30 | Inspect gutters and remove any debris
40 | Flush water distribution system
50 | Remove all dirt and debris from the media pads
60 | Flush water distribution headers
70 | Drain and Disinfect the entire water distribution system
80 | Findings Reported To Maintenance Supervisor

## NH3-CD-A-02
NH3-CD-A-02 | ANNUAL WATERLESS ADIABATIC COOLING SYSTEM SHUTDOWN
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Visually inspect cleanliness and stability
30 | Inspect gutters and remove any debris
40 | Flush water distribution system
50 | Remove all dirt and debris from the media pads
60 | Flush water distribution headers
70 | Drain and Disinfect the entire water distribution system
80 | Findings Reported To Maintenance Supervisor

## NH3-CD-M-01
NH3-CD-M-01 | MONTHLY WATERLESS ADIABATIC COOLING SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Visually inspect cleanliness and stability
30 | Inspect gutters and remove any debris
40 | Check water distribution for leaks and clogged orifices in the distribution header
50 | Flush water distribution system
60 | Check water flow rate and adjust if necessary
70 | Check water distribution is even across entire length of unit
80 | Remove all dirt and debris from the media pads
90 | Flush water distribution headers
100 | Drain and Disinfect the entire water distribution system (every 3 months)
110 | Findings Reported To Maintenance Supervisor

## MUA-M-01
MUA-M-01 | MONTHLY MAKE UP AIR UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect Belt Tensioning and Alignment, Adjust if required
30 | Check All Setscrews On Pulleys, Bearings, Shafts, And Fans
40 | Check Dampers And Damper Settings
50 | Check Control System
60 | Check for Glycol Heating Coil Leaking or not
70 | Check Filters and Replace as required
80 | Clean Debris in Filter Chambers
90 | Check Temperature of Bearings and Motors
100 | Findings Reported To Maintenance Supervisor

## RAD-DET-A-01
RAD-DET-A-01 | ANNUAL RADIATION DETECTOR INSPECTION
Sequence | Description
0 | Work is to be coordinated by City with Contractor prior to commencement of PM
10 | Inspect for any exposed wiring that may create a danger.
20 | Inspect system wiring or nicks and any loose connection.
30 | Check for water leakage or metal corrosion.
40 | Check sensor alignment.
50 | Clean sensor if needed.
60 | Trigger each sensor.
70 | Record your findings for item 10-60 in the report.
80 | Check system battery.
81 | It should be greater than 10.75 volts with system fully running without AC power
82 | +15 volts +/- 0.25 volts at pin 1 of P1 (reference to ground - pin3)
83 | +5 volts +/- 0.25 volts at pin 1 of P1 (reference to ground - pin3)
90 | Check system parameters.
100 | Print copy of system parameters for your record.
110 | Check system time and computer time. Both should be the same.
120 | Reboot system and check system time. Time should remain the same.
130 | Replace coin battery if needed.
140 | Perform source reading.
150 | Compare source reading to last year to see if there is any significate drop.
160 | Calculate efficiencies reading. Should be greater than 4%.
170 | Set off alarm and see if horn and strobe goes off.
180 | Check PC to see if storage space is adequate.
190 | Check PC to see if system logs are being stored daily.
200 | Using data viewer in PC to review events.
210 | Complete report and email client.
10 | Perform operational check using the radiation check source for proper alarm func
20 | Place one hand in front of the infrared sensor
30 | Position the check source over the sticker on the detector
40 | a. The CHECKING light on the remote display should now be lit
50 | the Supervisor software should show that the lane is occupied
60 | After 3-4 sec, remove the source from the detector and your hand from sensor.
70 | Verify that the alarm circuit is activated, by checking alarm light is on
80 | Any other remote alarm indicators should also be activated
90 | the Supervisor software (if used) should display an alarm “popup” message
100 | Press the ALARM RESET button
110 | or wait until the alarm automatically clears.
120 | All alarm indicators should go off, including any remote strobe or horn
130 | The “popup” alarm window must be cleared manually or click “X”
140 | Repeat the procedure for any other active radiation detector
150 | Clean the infrared occupancy sensors front lenses using a soft cloth and water

## MECH-AS-A
MECH-AS | ANNUALLY AIR SEPARATOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Open the blowdown drain valve to remove the loose sediment
30 | Check the pressure drop across the separator
40 | Isolate the separtor and clean the strainer when increaed in pressure drop
50 | Findings Reported To Maintenance Supervisor

## RAD-DET-W-01
RAD-DET-W-01 | WEEKLY RADIATION DETECTOR INSPECTION
Sequence | Description
10 | Perform operational check using the radiation check source for proper alarm function
20 | Place one hand in front of the infrared sensor
30 | Position the check source over the sticker on the detector
40 | a. The CHECKING light on the remote display should now be lit
50 | the Supervisor software should show that the lane is occupied
60 | After 3-4 sec, remove the source from the detector and your hand from sensor.
70 | Verify that the alarm circuit is activated, by checking alarm light is on
80 | Any other remote alarm indicators should also be activated
90 | the Supervisor software (if used) should display an alarm “popup” message
100 | Press the ALARM RESET button
110 | or wait until the alarm automatically clears.
120 | All alarm indicators should go off, including any remote strobe or horn
130 | The “popup” alarm window must be cleared manually or click “X”
140 | Repeat the procedure for any other active radiation detector
150 | Clean the infrared occupancy sensors front lenses using a soft cloth and water

## PU-CIRC-A-01
PU-CIRC-A-01 | ANNUALLY CIRCULATION PUMP INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect pump in proper operation and mention any abnormalities or leaks
30 | Blow out motor windings with compressed air
40 | Inspect pump coupling and alignment
50 | Lubricate motor and pump bearings
60 | Inspect and clean associated pump strainer or filters
70 | Inspect electrical connections and mounting hardware
80 | Touch up damaged surfaces
90 | Check motor contactor for pitting or damages. Repair or replace as needed
100 | Check for proper fluid flow. Repair for fluid leaks as needed
110 | Check phase rotation
120 | Check insulation, vibration isolators and flexible connectors
130 | for integrity. Repair as needed.
140 | Discharge Pressure +/- 10% of full flow
150 | Suction Pressure +/- 10% of full flow
160 | Motor Amperage: ________Amp
170 | Motor Voltage: _________Volt
180 | VFD Frequency: ________Hz (if applicable)
190 | Findings Reported To Maintenance Supervisor

## CE-POOL-PU-Q
PD-POOL-PU-Q | QUARTERLY POOL CIRCULATION PUMP INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect pump in proper operation and mention any abnormalities or leaks
30 | Inspect pump coupling and alignment
40 | Lubricate motor and pump bearings
50 | Inspect and clean associated pump strainer or filters
60 | Inspect electrical connections and mounting hardware
70 | Touch up damaged surfaces
80 | Check motor contactor for pitting or damages. Repair or replace as needed
90 | Check for proper fluid flow. Repair for fluid leaks as needed
100 | Check insulation, vibration isolators and flexible connectors for integrity. Repair as needed.
110 | Discharge Pressure +/- 10% of full flow
120 | Suction Pressure +/- 10% of full flow
130 | Motor Amperage: ________Amp
140 | Motor Voltage: _________Volt
150 | VFD Frequency: ________Hz (if applicable)

## PD-PU-A
PU-CIRC-A-01 | ANNUAL CIRCULATING PUMP INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect pump in proper operation and mention any abnormalities or leaks
30 | Blow out motor windings with compressed air
40 | Inspect pump coupling and alignment
50 | Lubricate motor and pump bearings
60 | Inspect and clean associated pump strainer or filters
70 | Inspect electrical connections and mounting hardware
80 | Touch up damaged surfaces
90 | Check motor contactor for pitting or damages. Repair or replace as needed
100 | Check for proper fluid flow. Repair for fluid leaks as needed
110 | Check phase rotation
120 | Check insulation, vibration isolators and flexible connectors
130 | for integrity. Repair as needed.
140 | Discharge Pressure +/- 10% of full flow
150 | Suction Pressure +/- 10% of full flow
160 | Motor Amperage: ________Amp
170 | Motor Voltage: _________Volt
180 | VFD Frequency: ________Hz (if applicable)
190 | Findings Reported To Maintenance Supervisor

## MUA-S-02-R21
MUA-S-02-R21 | SEMI-ANNUAL MAKE UP AIR UNIT INSPECTION (RFP)
Sequence | Description
10 | Complete Pre Job Hazard Assessment
20 | Perform pre-work CO and gas safety check
30 | Check electrical components and wiring
40 | Inspect Belt Tensioning, adjust if required
50 | Check All Setscrews On Pulleys, Bearings, Shafts, And Fans
60 | Check local Control System
70 | Inspect And Clean Burners And Burner Controls
80 | Lubricate blower motor, damper louvres and fan bearings
90 | Check control enclosure ventilation if applicable
100 | Check outdoor air intakes, screens and adjacent area for cleanliness
110 | Check Damper, damper Motor and linkagesfor proper operation
120 | Check & clean static pressure sensor
130 | Check Motor & Fan Pulleys Are Properly Aligned and secured
140 | Check Roof Curb For Damage
150 | Check All Panels On Unit For Tightness
160 | Check Gaskets On Access Doors
170 | Check Isolation On Fan
180 | Check & clean metal pre-filter
190 | Check Gas Pressures
200 | Check Guard On Motor Is Secure
210 | Check and clean Burner Screen
220 | Check Automatic Shutdown Controls and Test Safety Shut-Off Vales
230 | Check Ignition Sequence
240 | Inspect coils and drain pan for cleanliness (if applicable)
250 | Inspect all filters including MERV 13, replace or clean as needed
260 | Water Coil to be drained & filled w/ anti-freezing fluid for Coil Winterization
270 | Perform post-work CO and gas safety check
280 | Findings Reported To City Representative
290 | ***For Make Up Air Unit in Fire Hall***
300 | Check proper operation, activation and function for MUA
310 | Verify interlock signal and control function between BMS & PLC control
320 | Test & verify interlock sequence of CO/NOx, MUA, general & vehicle exhaust & OHD

## MUA-A-01
MUA-A-01 | ANNUALLY MAKE UP AIR UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Wiring For Condition & Connection Tightness
30 | Check Mag Starter & Holding Contacts
40 | Check Control Contactors & Clean Or Replace As Required
50 | Check Current Protection Devices A
60 | Check Voltage Protection Devices V
70 | Check Interlock Operation
80 | Check Remote Panel Contactors & Operational Lights
90 | Check Modulating Gas Valve For Operation
100 | Check Low Voltage Circuitry
110 | Blow Out Motor Windings, If Required
120 | Lube Blower Motor, If Required
130 | Lube Damper Louvres, If Required
140 | Lube Fan Bearings, If Required
150 | Check Damper & Motor Operation
160 | Check Ductstat Setting & Clean
170 | Check Motor & Fan Pulleys Are Properly Aligned
180 | Check Motor Pulley Is Secured To Shaft
190 | Check Roof Curb For Damage Or Wear
200 | Check All Panels On Unit For Tightness
210 | Check Gaskets On Access Doors & Replace As Required
220 | Check Isolation On Fan
230 | Check Birdscreen & Clean As Required
240 | Check Gas Pressures
250 | Check Guard On Motor Is Secure
260 | Check Burner Screen & Clean As Required
270 | Check Automatic Shutdown Controls and Test Safety Shut-Off Vales
280 | Check Ignition Sequence
290 | Inspect coils and drain pan for cleanliness (if applicable)
300 | Clean or change filters
310 | Water Coil to be drained and filled with anti-freezing or suitable fluid for Coil Winterization (if applicable)
320 | Findings Reported To Maintenance Supervisor

## EL-EVS-A
EL-EVS-A | ANNUAL ELECTRIC VEHICLE EQUIPMENT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 9 requirement for inspection
30 | ***Visual and Mechanical Inspection***
40 | Check the integrity of operating meters, capacitors and cables
50 | Check for corrosion of unit, abnormal sounds and odors
60 | Check for ventilation obstruction and clean vents
70 | Replace filter as needed
80 | Check any discoloured of connectors, Tighten as needed
90 | ***Electrical***
100 | Check and record the output voltage on battery terminal and output current
110 | Check the integrity of capacitor if equipped. Replace as needed (5-7 years)
120 | Check for ground leakage in floating equipment by measuring the dc voltage readings
130 | Replace surge protectors as needed
140 | ***Operation***
150 | Check alarm setting and meter readings against the battery manufacturer's requirement
160 | Check the float voltage
170 | Equalize voltage at the battery terminal to correct adjustment. Readjust setting as needed
180 | Test the function of charge mode operation

## HUM-A-01
HUM-A-01 | ANNUAL HUMIDIFIER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check Wiring For Condition & Connection Tightness
20 | Check Low Voltage Transformer & Circuitry
30 | Check Heating Coils For Calcium Build-Up & Clean As Required
40 | Check Tank For Calcium Build-Up & Clean As Required
50 | Check Water Level In Tank Is Correct
60 | Check For Excess Dirt, Grease Or Corrosion, Clean As Required
70 | Check Fan Cage Is Secured To Motor Shaft
80 | Check & Clean Humidistat
90 | Check Operation Of Solenoid Valve
100 | Check & Drain Tank
110 | Check & Clean Float
120 | Check Valve Operation & Leakage
130 | Check Hangers For Level, Clean, Tighten Or Adjust As Required
140 | Check Fan Is Secured To Unit
150 | Check ultraviolet lamp. Clean or replaced as needed
160 | Check proper fluid flow and for fluid leaks
170 | Measure relative humidity and adjust the system as needed
180 | Check and clean steam system traps
190 | Check pumps and controls in proper operation
200 | Check for fouling, corrosion or degradation. Clean or repair as needed
210 | Check strainers. Clean as needed
220 | Visually inspect distributors, nozzles and drain pans for biological growth. Clean or disinfect as needed
230 | Findings Reported To Maintenance Supervisor
Existing task in EAM
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check Wiring For Condition & Connection Tightness
20 | Check Low Voltage Transformer & Circuitry
30 | Check Heating Coils For Calcium Build-Up & Clean As Required
40 | Check Tank For Calcium Build-Up & Clean As Required
50 | Check Water Level In Tank Is Correct
60 | Check For Excess Dirt, Grease Or Corrosion, Clean As Required
70 | Check Fan Cage Is Secured To Motor Shaft
80 | Check & Clean Humidistat
90 | Check Operation Of Solenoid Valve
100 | Check & Drain Tank
110 | Check & Clean Float
120 | Check Valve Operation & Leakage
130 | Check Hangers For Level, Clean, Tighten Or Adjust As Required
140 | Check Fan Is Secured To Unit
150 | Change of canister
160 | Findings Reported To Maintenance Supervisor

## MECH-IH-S
MECH-IH-S | SEMI-ANNUALLY INFRARED HEATER INSPECTION
Sequence | Description
10 | Inspect All Burners And Check Their Condition.
20 | Visual Check Pilot Sensor, Shield, Spark Plug If Excessive Carbon Residue, Record.
30 | Visually Check Ceramic Retainer Grid For Carbon Build-Up And Cracks.
40 | Check Burner Observation Window And Firing Tube, Gaskets For Damage.
50 | Check Air Filter, Vacuum Pump, Airflow Switch And Condensate Trap.
60 | Inspect All Radiant Tubes For Blockages, Perforations, Corrosion
70 | Inspect All Tailpipes, Fittings For Blockages, Perforations, Corrosion
80 | Inspect All Deflector Panels For Proper Alignment.
90 | Start System And Check Performance Of Unit.
100 | Using A Portable Co Detector, Inspect All Accessible Intake Tighten As Required.
110 | Use Portable Co Detector, Inspect Accessible Ductwork & Connections.
120 | Use Portable Co Detector, Inspect Accessible Exhaust Flanges & Connections.
130 | Record Any Abnormalities.
140 | Contact Facility Management If Any Major Leaks Or Co Emissions Are Detected
150 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
160 | Pre Job Hazard Assessment Completed?

## PLSE-A-01
PLSE-A-01 | ANNUAL FALL PROTECTION PERSONAL EQUIPMENT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Qualified Vendor To Select Relevant PM Task According To Personal Equipment
30 | *******ENERGY (SHOCK) ABSORBER & LANYARD INSPECTION*******
40 | Keep free from substance and condition to avoid deterioration of equipment
50 | Re-certified as specified by manufacturer if needed
60 | Approved by CSA Standard Z259.11-05, Energy absorbers and lanyards
70 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for
80 | personal fall arrest systems, subsystems and components
90 | Class E4: Standard 4.0 kN energy absorber or lanyard intended for
100 | general use in fall arrest systems. For workers from 100 lb. to 254 lb.
110 | Class E6: Heavyweight 6.0 kN energy absorber or lanyard intended for
120 | use in fall arrest systems for workers from 200 lb. to 386 lb.
130 | Do not store around chemicals and wet place
140 | Select the shortest length lanyard not interfering work performance of duties
150 | *******LIFE SAFETY ROPE INSPECTION*******
160 | Meet CSA Standard CAN/CSA-Z259.2.1-98 (R2004), Fall Arresters,
170 | Vertical Lifelines, and Rails Approved by NFPA Standard 1983,
180 | Standard on Life Safety Rope and Equipment for Emergency Services
190 | Keep free from substance and condition to avoid deterioration of equipment
200 | Re-certified as specified by manufacturer if needed
210 | Life safety rope extends downward to within 1.2 meters of ground level
220 | Free of knots or splices throughout the travel portion
230 | Material appropriate to hazard and able to withstand adverse effect
240 | Minimizes the hazard of swinging and limits the swing
250 | drop distance to 1.2 meters if worker falls
260 | *******FULL BODY HARNESS INSPECTION*******
270 | Approved by CSA Standard CAN/CSA Z259.10-06, Full Body Harnesses
280 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for
290 | personal fall arrest systems, subsystems and components
300 | Keep free from substance and condition to avoid deterioration of equipment
310 | Re-certified as specified by manufacturer if needed
320 | *******FALL ARRESTOR INSPECTION*******
330 | Fulfill CSA Stdard Z259.2.1-98 (R2004), Fall Arrest., Vertical Lifelines & Rails
340 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for
350 | personal fall arrest systems, subsystems and components
360 | Keep free from substance and condition to avoid deterioration of equipment
370 | Re-certified as specified by manufacturer if needed
380 | Remove from service if it is defective, contact with heat,
390 | chemical and any substance that may corrode
400 | Remove from service after personal fall arrestor system has stopped a fall
410 | Do not use unless a prof. engineer or manufacturer certifies the system is safe
420 | *******SELF RETRACTING DEVICE INSPECTION*******
430 | Approved by CSA Standard Z259.2.2-98, Self-Retracting
440 | devices for Personal Fall-Arrest Systems
450 | Keep free from substance and condition to avoid deterioration of equipment
460 | Re-certified as specified by manufacturer if needed
470 | Minimizes the hazard of swinging and limits the swing
480 | drop distance to 1.2 meters if worker falls
490 | *******CARABINER AND SNAP HOOKS INSPECTION*******
500 | Must be inspected by worker before it is used on each shift
510 | Keep free from substance and condition to avoid deterioration of equipment
520 | Re-certified as specified by manufacturer if needed
530 | Carabiner or snap hook is self closing and self-locking
540 | Opened by at least two consecutive deliberate actions
550 | Marked with its breaking strength in major axis
560 | Marked with the name or trademark of manufacturer
570 | ***********************************************************************
580 | Findings Reported To Maintenance Supervisor

## SD-M-01
SD-M-01 | Monthly Smoke Detector Inspection
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per NFPA 72 - National Fire Alarm and Signalling Code and Manfacturer's instruction for inspection
30 | Provision of scissor lift with proper PPE for high level working area if applicable
40 | Smoke detector is powered by: Hardwired Conventional Battery Non-Replaceable Long-Life Batteries (10 yrs)
50 | Battery Expiry Date: (If applicable)
60 | Replace the Non-Replaceable Long-Life Batteries (10 yrs) smoke detector when its lifecycle is completed
70 | Smoke detector alarm is securely fastened to the wall or ceiling
80 | Smoke detector alarm shows no evidence of physical damage, paint, application or excessive grease and dirt accumulations
90 | Ventilation holes on the smoke detector alarm are clean and free of obstructions
100 | Test smoke detector alarms once a month by pressing the test button and replacing the batteries as required.
110 | Smoke detector alarm signal sounds when the test device is operated
120 | If that smoke detector alarm "chirps" which warning the battery is low, replace the battery right away.
130 | Findings Reported To Maintenance Supervisor
Smoke alarms should be maintained according to manufacturer’s instructions.
Test smoke alarms at least once a month using the test button.
Make sure everyone in the home understands the sound of the smoke alarm and knows how to respond.
Follow manufacturer’s instructions for cleaning to keep smoke alarms working well. The instructions are included in the package or can be found on the internet.
Smoke alarms with non-replaceable 10-year batteries are designed to remain effective for up to 10 years. If the alarm chirps, warning that the battery is low, replace the entire smoke alarm right away.
Smoke alarms with any other type of battery need a new battery at least once a year. If that alarm chirps, warning the battery is low, replace the battery right away.
When replacing a battery, follow manufacturer’s list of batteries on the back of the alarm or manufacturer’s instructions. Manufacturer’s instructions are specific to the batteries (brand and model) that must be used. The smoke alarm may not work properly if a different kind of battery is used.

## HI-01
HI-01 | ANNUAL INFRARED HEATER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Inspect All Burners And Check Their Condition.
20 | Visual Check Pilot Sensor, Shield, Spark Plug, If Carbon Residue, Record.
30 | Visually Check Ceramic Retainer Grid For Carbon Build-Up And Cracks.
31 | Remove any carbon deposit or scale on ceramic retained grid by wire brush
40 | Check Burner Observation Window And Firing Tube, Gaskets For Damage.
50 | Check function of Vacuum Pump, Airflow Switch And Condensate Trap.
60 | Inspect All Radiant Tubes and Couplings for Blockages, Perforations, Corrosion
70 | Inspect All Tailpipes, For Blockages, Perforations, Corrosion
80 | Inspect All Fittings And Couplings For Blockages, Perforations, Corrosion
90 | Inspect And Check Deflector Panels For Proper Alignment.
100 | Using Portable Co Detector, Inspect All Accessible Intake And Exhaust Flanges
110 | Using Portable Co Detector, Inspect All Accessible Ductwork And Connections
120 | Record Any Abnormalities.
130 | Contact Facility Management If Any Major Leaks Or Co Emissions Are Detected
140 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
150 | Ensure All Radiant Tubes Are Properly Connected And Suspended Securely
160 | Check for dirt or dust for filers, clean or replace as required
170 | Findings reported to Maintenance Supervisor

## PD-MV-Q
PD-MV-Q | QUARTERLY MIXING VALVE INSPECTION
Sequence | Description
10 | Use proper protective equipment for eyes and skin
20 | Shut off hot and cold water supply valve
30 | Remove valve's top cap, pull out thermostat and use the push rod to test the piston
40 | Remove the control section assembly, top cap and thermostat.
50 | Unthread the liner from the cap
60 | Clean the piston and liner with non-corrosive agent or any cleaner suitable for brass and stainless steel. DO NOT USE ABRASIVES.
70 | Push the mechanism up and down several times to make sure the piston moves smoothly and consistently.
80 | Remove the stop and check valves, clean any collected deposits from strainer and valve seat with brush and non-corrosive cleaning solution
90 | Reassembly the valve
100 | Reset the water temperature by adjustment of temperature set screw (Factory setting is 40.5 Deg.C) if needed
110 | Turn on hot and cold water supply valve

## PD-HX-A
HX-A-01 | ANNUAL HEAT EXCHANGER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check For Any Fluids Or Leaks At All Valves, Welds, Unions And Fittings.
20 | Have The Office Of Capital Staff Stroke Control Valve From Full Open/Full Closed
30 | Set Return Control Valve To Auto Observe Valve Operator, Record Observations.
40 | Check Control Valve For Leaks.
50 | Keep Valve Open And Record Boiler Heating Fluid: Return:
60 | Keep Valve Open And Record Boiler Heating Fluid: Supply:
70 | Keep Valve Open Record Heated Fluid (Pool Water Or Domestic Hot Water): Return:
80 | Keep Valve Open Record Heated Fluid (Pool Water Or Domestic Hot Water): Supply:
90 | Have Site Foreman Provide Bas Temperature (Boiler Heating Fluid). Bas Return:
100 | Have Site Foreman Provide Bas Temperature (Boiler Heating Fluid). Bas Supply:
110 | (Where Applicable) Record Bas Operating Set Point Temperature:
120 | If Thermometer And Bas Readings Are Different By More Than 1 Degree F Record
130 | Clean Exterior Of Exchanger.
140 | Findings Reported To Maintenance Supervisor

## HX-01
HX-01 | ANNUAL HEAT EXCHANGER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check For Any Fluids Or Leaks At All Valves, Welds, Unions And Fittings.
20 | Have The Office Of Capital Staff Stroke Control Valve From Full Open/Full Closed
30 | Set Return Control Valve To Auto Observe Valve Operator, Record Observations.
40 | Check Control Valve For Leaks.
50 | Keep Valve Open And Record Boiler Heating Fluid: Return:
60 | Keep Valve Open And Record Boiler Heating Fluid: Supply:
70 | Keep Valve Open Record Heated Fluid (Pool Water Or Domestic Hot Water): Return:
80 | Keep Valve Open Record Heated Fluid (Pool Water Or Domestic Hot Water): Supply:
90 | Have Site Foreman Provide Bas Temperature (Boiler Heating Fluid). Bas Return:
100 | Have Site Foreman Provide Bas Temperature (Boiler Heating Fluid). Bas Supply:
110 | (Where Applicable) Record Bas Operating Set Point Temperature:
120 | If Thermometer And Bas Readings Are Different By More Than 1 Degree F Record
130 | Clean Exterior Of Exchanger.
140 | Findings Reported To Maintenance Supervisor

## HRU-A-01
HRU-A-01 | ANNUAL HEAT RECOVERY UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Vacuum and wash standard foam filters, Replace as needed
30 | Wash the foil faced insulation surface and wipe the drain pan
40 | Check for proper operation of heat exchanger. Clean or replace as needed
50 | Check and clean blower wheels and fan housing
60 | Check all control modes for proper operation
70 | Check damper for proper operations, condition and setting. Repair and adjust as needed
80 | Check fan belt tension. Replace as needed
90 | Assess field serviceable bearings. Lubricate as needed
100 | Check P-trap drain. Clean as needed
110 | Touch up any corrosive and damaged surface
120 | Findings Reported To Maintenance Supervisor

## CE-NDE-S
CE-NDE-S | SEMI-ANNUALLY NEDERMAN DIESEL EXHAUST SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check and inspect the trolley could move easily along the length of the rail,
30 | Clean the guide ways if necessary
40 | Check condition of trolley wheels
50 | Make sure hose lifts properly and adjust the trolley balancer of lifting power if necessary
60 | Check and inspect the cord and plastic pipe condition
70 | Check protective strip
80 | Check horizontal hose condition
90 | Check vertical hose condition
100 | Check overall condition of all hoses, connections, clamps & clips.
110 | Make sure nozzle is pointing forward in the driving direction when not connected to the fire truck
120 | Check electro magnet condition, attachment, electrical connections and functionality.
130 | Clean magnet and anchor plate on truck
140 | Check HB nozzle overall condition, clean interior and internal surface contact
150 | Check operation of disconnection box
160 | Make sure the disconnection of hose from the exhaust pipe immediately before the fire truck leaves the fire hall door
170 | Check transformer operation
180 | Check electrical contacts operation
190 | Check electrical components operation
200 | Check proper operation, activation and function for exhaust fan, measure air flow if necessary
210 | Check proper operation for end stop of track or rails, trolley stop and shock absorber
220 | Check condition of hanger
230 | Check condition of truck anchor plate
240 | Check operation of all switches, relays, contactors, breakers, transformers and connections.
250 | Tighten all wiring connections if necessary
260 | Check overall condition of exhaust duct, mechanical supports and air leaks in connections.
270 | Submission of inspection report and record any deficiencies

## ARC-FE-A
ARC-FE-A | ANNUAL FENCE EXTERIOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | The installed posts are plumb.
30 | The corners and the ends of the posts are firm and are supported and anchored well.
40 | The tension wires and fabrics used are placed in a proper gage and are secure.
50 | The gates should move and swing freely without binding if equipped.
60 | Fence rails must extend posts with both ends.
70 | Woodend posts, pickets, and rails must be free from rot, and sealed well.
80 | All hardware should be free from rust.
90 | Check for any faded paint, chipped paint, deficient powder coating, and/or stain.
100 | Check any graffiti or damages on fence, correct as needed.
110 | Check the alignment of fence, correct as needed.
120 | Check for any damaged mesh if equipped.
130 | Check for any loosen parts, tighten as needed.
140 | Check for missing caps.
150 | Check for bent, dented or damaged post and rails, correct as needed.

## ARC-SNOW-W
ARC-SNOW-W | WEEKLY SNOW REMOVAL
Sequence | Description
10 | Inspect and wear all personal protective equipment and warm winter clothing.
20 | Use the snow blower to remove all snow from the entrance ways, sidewalks and paths first.
30 | Apply additional salt/sand or ice melt to shady areas or spots where ice is likely to form
40 | Ice melting products should be applied in accordance with manufacturer’s recommendations.
50 | Inspect the premises to ensure clearing of ice/snow or other necessary maintenance is done
60 | Inspect railings, stairs, ramps and other foot traffic areas to ensure they are in good condition
70 | Inspect sidewalk blocks or concrete/asphalt surfaces to ensure there are no tripping hazards
80 | Remove snow as soon as possible from the roof. Do not let it pile up along the edges
90 | Ensure downspouts or water collection containers positioned away from footpaths
100 | Clean off all equipment and return it to the appropriate storage area.
110 | Close bag of salt, lava rock or deicer, and return to storage.
3

## CE-WS-A
CE-WS-A | ANNAUL WEIGHT SCALE ACCURACY INSPECTION
Sequence | Description
10 | Refer to Inspection and testing requirement by Alberta Transportation
20 | To carry out the following inspection and test in the presence of consultant
30 | To carry out the weight test and strain load test
40 | Record all test parameters, results and error (should be within +/- 10 KG)
50 | Check the condition of drainage
60 | Check the condition of approaches
70 | Check the condition of moving parts clear and level
80 | Check ends of deck clear
90 | Check beam condition and clearance
100 | Check beam shack installation
110 | Check sensitivity of zero
120 | Check sensitivity of full load
130 | Check seals and marking
140 | Submission of Scale Accuracy Inspection Form with consultant's details to Measurement Canada Office
150 | Name and address of contractor
160 | Make, model and serial number of devices
170 | Capacity of device
180 | Address and description of the location of device installed
190 | Consultant forward the copy of the results to Alberta Transportation Project Administator

## SG-S-01
SG-S-01 | SEMI-ANNUALLY SLIDING GATE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refers to manufacturer's requirement for maintenance
30 | ***General Gate Condition***
40 | Check for physical damage
50 | Check condition of rollers and other moving parts
60 | Check roller alignment and tightening shaft bolt
70 | Ensure gate rolls free by hand
80 | ***Gate Operator*** (if applicable)
90 | Inspect, adjust, lubricate drive chain
100 | Inspect brake assembly
110 | Inspect clutch
120 | Check condition of sprockets, gear, drive chain
130 | Check condition of V-belt, replace as needed
140 | Check proper operation of run gate
150 | Tighten all set screws and bolts
160 | Inspect all nuts and bolts for proper tightness
170 | Check limits
180 | Lubricate limit chain / shaft as needed
190 | Ensure gate caution sign is present
200 | Check battery backup system if equipped
210 | Inspect all electrical wiring condition
220 | ***Safety Component***
230 | Test all controls operates properly
240 | Test all internal sensors and external safety system
250 | Check the photo eye alignment
260 | Check the function of emergency stop
270 | Findings Reported To Maintenance Supervisor

## IRR-S-01
IRR-S-01 | SEMI-ANNUALLY IRRIGATION SPRINKLER INSPECTION
Sequence | Description
10 | START UP (Spring):
20 | Inspect system for obvious damages
30 | Visually check main line for leaks
40 | Inspect valve boxes for leaks
50 | Run through each zone through the controller
60 | Adjust heads for proper arc and throw
70 | Inspect for leaks as each zone runs
80 | Inspect wiring to valve boxes and controller
90 | Make deficiencies list to be quoted and approved by the client prior to repairs
100 | Test associated backflow preventors
110 | WINTERIZATION (Winter):
120 | Isolate irrigation water source for the winter
130 | Turn off controller
140 | Clear all underground system of water

## LS-RA
LS-RA | Restricted Area Inspection
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Occupational Health and Safety Code Part 5 requirement for inspection
30 | To identify all existing and potential restricted space at work site
40 | To identify and assess the hazards to the workers
50 | To identify the PPE and emergency equipment to be used
60 | Ensure all workers is trained by competent person in performing their duties in safe and healthy manner
70 | Ensure first aid kits, use of emergency equipment and safety procedures in place
80 | Follow the Entry permit system and
90 | Verify the oxygen content is between 19.5-23% if applicable
100 | To identify the amount of toxic, flammable or explosive substance present if applicable
110 | Provision of ventilation and purging if needed
120 | Ensure safety means of entry and exit is available to all workers
130 | Designate competent tending worker to communicate with workers in restricted area
140 | Ensure evacuation procedures in emergency response plan is present
150 | Retaining proper records for entry and work in restricted area

## BWS-A-01
BWS-A-01 | ANNUAL BULK WATER STATION ELECTRICAL INSPECTION
Sequence | Description
10 | Please contact the vendor to perform the annual PM
20 | Coordinate with Water Services personnel for scheduling purposes
30 | Assist the vendor on the site if needed
40 | Conduct an electrical inspection on the Card Lock system
50 | Perform a Heat Scan on the electrical panels and equipment
60 | Report any abnormalities found

## BWS-W-01
BWS-W-01 | WEEKLY BULK WATER STATION ROUNDS
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Clean and pick-up garbage inside the fence lot
20 | Do a yard light sweep and replace for burnt bulbs and parts as requested
30 | Check the salt bin and refill if needed (Winter)
40 | Apply some salt and sand in the surrounding re-filling station (Winter)
50 | Visual inspect drainage under grates and report any abnormalities
60 | Visual and function check on the Card Lock system and report any abnormalities
70 | Do a visual check on the Truck Filling system and report any abnormalities
80 | De-ice the discharge valve (Winter)
90 | Ensure the heat trace system is ON in Fall (if applicable)
100 | Ensure the heat trace system is OFF in Spring (if applicable)
110 | Lubricate piping system with associated piping valves and connections if need
120 | Re-set card reader in winter months when the display blacks out if need
130 | Visual inspection of parking lot lighting standard
140 | Avoid flight path obstruction on top of lighting standard
150 | Findings reported to Maintenance Supervisor

## BWS-A-02
BWS-A-02 | ANNUAL BULK WATER STATION MECHANICAL INSPECTION
Sequence | Description
10 | Please contact the vendor to perform the annual PM
20 | Coordinate with Water Services personnel for scheduling purposes
30 | Assist the vendor on the site if needed
40 | Conduct an inspection on the Aqualoader truck fill system (if equipped)
50 | Inspect and check for leaks on the valve system assemblies
60 | Report any abnormalities found

## WB-W-01
WB-W-01 | Weekly Washbay Inspection
Sequence | Description
10 | Check OHD for proper operation including the card reader if equipped
20 | Check the operation/condition of the vacuum hoses, filter
30 | Clean the area (empty garbage cans), Inspect sump pits
40 | Check the condition of lids and grates, walls and lights
50 | Check the condition of the hoses, spray guns and holder, signage
60 | Visual inspection of the pressure washer, softener and heater for leaks, damages
70 | Replace in-line bag filter if equipped and if needed
80 | Assist vendors at washbay to clean out troughs and sumps, as required
90 | Measure the solid level in the sump
100 | Measure the liquid level in holding tank (if applicable)
110 | To determine cleaning services if needed

## STAIR-A-01
STAIR-A-01 | ANNUAL METAL STAIRS INSPECTION
Sequence | Description
10 | Inspect exterior stairs for any damages
20 | Ensure the integrity of the traction coating on stair nosing is in good order
30 | Report any observed issues to Facility Operations for approval on correction

## EL-CPLUG-A
EL-CPLUG-A | ANNUAL PARKING PLUGS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check car plugs connections, fuse and circuit breakers for normal condition
30 | Check the voltage in the receptacle

## LFT-DLV-S-01
LFT-DLV-S-01 | SEMI-ANNUAL DOCK LEVELER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual and ANSI MH30.1 standard requirement for inspection
30 | Below task plan is the minimum requirement to follow. Contractor is responsible
40 | to comply with all updated and applicable codes as required
50 | Power on the leveler & check for sign of mechanical malfunction during operation
60 | Inspect for handle or chain for damage if dock leveler is mechanically operated
70 | Shut the power off before performing the following maintenance
80 | Walk around the dock leveler and take note of obvious damage that
90 | may have been caused by operation during the last shift
100 | Check that all capacity, safety, identif. plates, etc. are attached and legible
110 | Inspect for damaged or missing parts, rust, corrosion, bent parts, cracks, etc.
120 | Carefully inspect the hinge points for cracks, breaks, bending, twists, and wear
130 | Inspect push button control station for visual damage
140 | With the dock leveler in stored position, clean away wood splinters, nails and
150 | any other debris from the upper lip hinged surface by sweeping with broom
160 | Check for missing or damaged dock bumper mounted on dock face
170 | Clean spills from the dock area floor & the dock leveler immediately when
180 | they are observed
190 | Inspect visually the dock leveler for signs of structural damage
200 | Check oil level. Add oil to the reservoir if necessary
210 | Check pivot bushing and pins for wear
220 | Make sure all pins are secure and retained
230 | Pivot shaft must not rotate; make sure set screws are not loose
240 | Check hydraulic lines for damage or leaking. Replace if damaged
250 | Check wiring damage. Replace immediately if any sign of wear is evident
260 | Bushings on pivot pins on cylinders are permanently lubricated and
270 | require no servicing
280 | ***************************************************
290 | Review and rectify defects in inspection report by contractor
300 | Findings Reported To Facility Maintenance Coordinator

## LFT-DLV-A-01
LFT-DLV-A-01 | ANNUAL DOCK LEVELER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual and ANSI MH30.1 standard requirement for inspection
30 | Below task plan is the minimum requirement to follow. Contractor is responsible
40 | to comply with all updated and applicable codes as required
50 | Power on the leveler & check for sign of mechanical malfunction during operation
60 | Inspect for handle or chain for damage if dock leveler is mechanically operated
70 | Shut the power off before performing the following maintenance
80 | Walk around the dock leveler and take note of obvious damage that
90 | may have been caused by operation during the last shift
100 | Check that all capacity, safety, identif. plates, etc. are attached and legible
110 | Inspect for damaged or missing parts, rust, corrosion, bent parts, cracks, etc.
120 | Carefully inspect the hinge points for cracks, breaks, bending, twists, and wear
130 | Inspect push button control station for visual damage
140 | With the dock leveler in stored position, clean away wood splinters, nails and
150 | any other debris from the upper lip hinged surface by sweeping with broom
160 | Check for missing or damaged dock bumper mounted on dock face
170 | Clean spills from the dock area floor & the dock leveler immediately when
180 | they are observed
190 | Inspect visually the dock leveler for signs of structural damage
200 | Check oil level. Add oil to the reservoir if necessary
210 | Check pivot bushing and pins for wear
220 | Make sure all pins are secure and retained
230 | Pivot shaft must not rotate; make sure set screws are not loose
240 | Check hydraulic lines for damage or leaking. Replace if damaged
250 | Check wiring damage. Replace immediately if any sign of wear is evident
260 | Bushings on pivot pins on cylinders are permanently lubricated and
270 | require no servicing
280 | ***************************************************
290 | Review and rectify defects in inspection report by contractor
300 | Findings Reported To Facility Maintenance Coordinator

## AEC-ST-01
AEC-ST-01 | SEPTENNIAL ANTI ENTRAPMENT COVER REPLACEMENT
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Verify the size, flow rate of new anti entrapment cover
30 | The new drain cover must to meet the ASME / ANSI National Standard.
40 | Evaluate the pool condition
50 | ***Scenario 1: Pool are fully drained out***
60 | Ensure the filtration system is turned off
70 | Unscrew the old drain, and pocket the screws.
80 | The new drain cover should be sized sufficiently to fit into the drain hole.
90 | Place it into middle of the drain area and securely mounted at correct position
100 | Follow the manufacturer instruction & requirement for replacement
110 | ***Scenario 2: Water maintained in Pool***
120 | Appoint industry professional to carry out the replacement work
130 | Ensure the filtration system is turned off and no suction in the drain
140 | Worker must equip with proper diving apparatus, tools and equipment
150 | Including scuba-diving gear on & go to the bottom of the pool.
160 | Unscrew the old drain, and pocket the screws
170 | The new drain cover should be sized sufficiently to fit into the drain hole
180 | Place it into middle of the drain area and securely mounted at correct position
190 | Follow the manufacturer instruction & requirement for replacement
200 | Turn back the filtration system on after replacement
210 | Submission of Certificate of Compliance for each new installed drain cover
220 | RC is responsible for completing, submitting, and retaining the following doc
230 | RC submit "Anti-Entrapment Compliance Plan for Public Swimming Pools’" to AHS
240 | FM must confirm to receive of all copy of submission as record
250 | Findings Reported To Facility Maintenance Coordinator

## IA-BMS-SENSOR-A
IA-BMS-SENSOR-A | ANNUAL BMS SENSORS INSPECTION
Sequence | Description
10 | FOLLOW-UP REPAIRS REQUIRED
20 | Inspect BAS sensor reading against the following:
30 | An alternate calibrated sensor device readout (ISO 9000 standard traceable)
40 | A buffer solution or gas at calibrated concentrations
50 | Actual damper position
60 | Allowable error – RH: +/-5.0
70 | Allowable error – DEG C: +/-1.0
80 | Calibration/verification of the automation points & end devices for each system
90 | Mixed air damper
100 | Outdoor air damper
110 | Mixed air temperature.
120 | Supply air temperature.
130 | Return air temperature.
140 | Space humidity.
150 | Space temperature.
160 | 0-10v signal on modulating gas valve.
170 | ON/OFF contacts on DX cooling relay.
180 | Carbon monoxide sensor
190 | Carbon Dioxide sensor
200 | Record observations below for all points listed above:
210 | Outdoor air damper - Pre Calibration Actual
220 | Outdoor air damper - Pre Calibration BAS
230 | Outdoor air damper - Post Calibration Actual
240 | Outdoor air damper - Post Calibration BAS
250 | Mixed air damper - Pre Calibration Actual
260 | Mixed air damper - Pre Calibration BAS
270 | Mixed air damper - Post Calibration Actual
280 | Mixed air damper - Post Calibration BAS
290 | Mixed air temp - Pre Calibration Actual
300 | Mixed air temp - Pre Calibration BAS
310 | Mixed air temp - Post Calibration Actual
320 | Mixed air temp - Post Calibration BAS
330 | Supply air temp - Pre Calibration Actual
340 | Supply air temp - Pre Calibration BAS
350 | Supply air temp - Post Calibration Actual
360 | Supply air temp - Post Calibration BAS
370 | Return air temp - Pre Calibration Actual
380 | Return air temp - Pre Calibration BAS
390 | Return air temp - Post Calibration Actual
400 | Return air temp - Post Calibration BAS
410 | Space humidity - Pre Calibration Actual
420 | Space humidity - Pre Calibration BAS
430 | Space humidity - Post Calibration Actual
440 | Space humidity - Post Calibration BAS
450 | Space temp - Pre Calibration Actual
460 | Space temp - Pre Calibration BAS
470 | Space temp - Post Calibration Actual
480 | Space temp - Post Calibration BAS
490 | Gas valve - Pre Calibration Actual
500 | Gas valve - Pre Calibration BAS
510 | Gas valve - Post Calibration Actual
520 | Gas valve - Post Calibration BAS
530 | DX cooling - Pre Calibration Actual
540 | DX cooling - Pre Calibration BAS
550 | DX cooling - Post Calibration Actual
560 | DX cooling - Post Calibration BAS
570 | CO sensor- Pre Calibration Actual
580 | CO sensor - Pre Calibration BAS
590 | CO sensor - Post Calibration Actual
600 | CO sensor - Post Calibration BAS
610 | CO2 sensor- Pre Calibration Actual
620 | CO2 sensor - Pre Calibration BAS
630 | CO2 sensor - Post Calibration Actual
640 | CO2 sensor - Post Calibration BAS

## IA-BMS-A
IA-BMS-A | ANNUAL BMS SYSTEM INSPECTION
Sequence | Description
10 | Verify communication operation
20 | Backup database of all network management related items
30 | Check battery status for network manager
40 | Verify proper opertaion of site with operator
50 | Do system verification report
60 | Verify last boot time of system
70 | Do visual/Audible inspection of PC and verify operation
80 | Verify proper communication
90 | Verify all inputs are properly calibrated and responding
100 | Verify non-critical digital outputs are switching properly
110 | Verify all critical digital inputs are switching with proper authorzation
120 | Verify all analog outputs are modulating properly
130 | Verify program backup of current system program is the most recent
140 | Backup if needed
150 | Verify all loop operation.
160 | Evaluate reaction of loop as compared to system needs
170 | Confirm with operatior that system has been functioning properly/investigate
180 | Check logs for abnormailities such as fast switching or dropoffs
190 | Check graphic for accuracy of point names and systems representation

## EF-A-01
MECH-EF | ANNUAL EXHAUST FAN INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Remove Cover From Unit.
20 | Vacuum Unit Thoroughly.
30 | Check Unit Fastening Devices To Ensure All Are Secure.
40 | Check fan blades, fan housing and belt guard condition
50 | Replace fan belt if needed
60 | Rotate Fan Wheel By Hand To Check Alignment Bearing Operation.
70 | Fan Wheel To Rotate Around Shaft, Without Binding Or Rubbing.
80 | Assess field serviceable bearings. Lubricate as needed
90 | Name Plate Data: Amps
100 | Name Plate Data: Volts
110 | Measured Data: Amps
120 | Measured Data: Volts
130 | Check motor contactor for pitting or damages. Repair or replace as needed
140 | Check integrity of flexible connections. Correct as needed
150 | Check Operating Lights. Replace Bulbs That Are Burnt Out.
160 | Check Proper Function in BMS if Equipped
170 | Findings Reported To Maintenance Supervisor
Existing task in EAM | MECH-EF
Sequence | Description
10 | Remove Cover From Unit.
20 | Vacuum Unit Thoroughly.
30 | Check Unit Fastening Devices To Ensure All Are Secure.
40 | Replace Belt.
50 | Rotate Fan Wheel By Hand To Check Alignment Bearing Operation.
60 | Fan Wheel To Rotate Around Shaft, Without Binding Or Rubbing.
70 | Turn On Disconnect Switch And Lubricate Motor As Per Mft’S Recommendations.
80 | Measure And Record Motor Amperage: 2-Speed Motors-Record Amperage At Both Speeds
90 | Name Plate Data: Low Speed: Amps
100 | Name Plate Data: Low Speed: Volts
110 | Name Plate Data: High Speed: Amps
120 | Name Plate Data: High Speed: Volts
130 | Measured Data: Low Speed: Amps
140 | Measured Data: Low Speed Volts
150 | Measured Data: High Speed: Amps
160 | Measured Data: High Speed V Olts
170 | Replace Unit Cover.
180 | Starter Shall Be Left In The Auto Position; Ensure All Are Running.
190 | Check Operating Lights. Replace Bulbs That Are Burnt Out.
200 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
210 | Pre Job Hazard Assessment Completed?

## MECH-VAV-A
MECH-VAV | ANNUAL VARIABLE AIR VOLUME BOX INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check for particulate accumulation on filters. Clean or replace as necessary to ensure proper operation.
30 | Check control system and devices for evidence of improper operation. Clean, lubricate, repair, adjust, or replace as needed
40 | Check for proper operation of cooling or heating coil and for damage or evidence of leaks. Clean, restore, or replace as needed
50 | Check for proper fluid flow. Clean, adjust, and repair as needed to restore proper flow.
60 | Check air filter fit and housing seal integrity. Correct as needed.
70 | Check fan blades and fan housing. Clean, repair, or replace as needed to ensure proper operation.
80 | Check integrity of all panels on equipment.
90 | Check the proper operation of dampers and actuators
100 | Ensure the operation in BMS if equipped
110 | Check the proper function of thermostat
120 | Replace fasteners as needed to ensure proper integrity and fit/finish of equipment.
130 | Check for proper damper operation. Clean, lubricate, repair, replace, or adjust as needed to ensure proper operation.
140 | Visually inspect areas of moisture accumulation for biological growth. If present, clean or disinfect as needed.
150 | Visually inspect exposed ductwork and external piping for insulation. Correct as needed.
160 | Findings Reported To Maintenance Supervisor

## UH-A-01
UH-A-01 | ANNUAL UNIT HEATER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Clean all dirt, lint, and grease from the combustion air opening and venter assembly.
30 | Inspect and clean all compartments, openings, fan blades, guards, coils & motors
40 | Check all unit component fastening devices are secure
50 | Check hangers and support hardware, tighten or adjust as required
60 | Replace belts - if applicable
70 | Check tension and condition of belts and pulley alignment
80 | Check electrical terminations, wiring & contactors are secure and all fuses inta
90 | Check all piping connections to unit for leaks
100 | Verify unit operation (including control valve where applicable)
110 | Clean all dirt, lint, and grease from the fan blade, fan guard, and motor.
120 | Clean the condensate traps.
130 | If it is a Gas Unit
140 | Inspect heat exchanger both internally and externally.
150 | Remove any external dirt or dust accumulation on heat exchanger
160 | Inspect and clean gas burner
170 | Inspect and clean ignition system and verify operation
180 | Check all piping connections to unit for leaks
190 | Check the vent/combustion air system for soundness.
200 | Clean openings. Replace any parts that do not appear sound.
210 | Inspect venting and combustion air piping for signs of corrosion and leakage
220 | All preventative maintenance to be performed as per manufacturer’s guidelines
230 | Findings Reported to Maintenance Supervisor
Existing tasks in EAM | UH-01
Sequence | Description
10 | Inspect and clean all compartments, openings, fan blades, guards, coils & motors
20 | Check all unit component fastening devices are secure
30 | Check hangers and support hardware, tighten or adjust as required
40 | Replace belts - if applicable
50 | Check tension and condition of belts and pulley alignment
60 | Check electrical terminations, wiring & contactors are secure and all fuses inta
70 | Check all piping connections to unit for leaks
80 | Verify unit operation (including control valve where applicable)
90 | If it is a Gas Unit
100 | Inspect heat exchanger
110 | Inspect and clean gas burner
120 | Inspect and clean ignition system and verify operation
130 | Check all piping connections to unit for leaks
140 | Inspect venting and combustion air piping for signs of corrosion and leakage
170 | All preventative maintenance to be performed as per manufacturer’s guidelines

## WTR-CHEM-BW-01
WTR-CHEM-BW-01 | BI-WEEKLY WATER TREATMENT TESTING
Sequence | Description
10 | Maintenance Personnel to collect water sample from HVAC system
20 | Submit the sample to a contractor who provides water testing

## WTR-CHEM-Q-01
WTR-CHEM-Q-01 | QUARTERLY WATER CHEMICAL TREATMENT FOR HVAC SYSTEM
Sequence | Description
10 | Maintenance Personnel to collect water sample from HVAC system
20 | Inspect, test, and record values for the following:
30 | Nitrates shall be maintained between 700 to 1500 ppm
40 | Molybdenum shall be maintained between 80 to 100 ppm
50 | pH shall be maintained between 8.0 and 10.5
60 | Conductivity/TDS shall not exceed 3600 µmhos
70 | Visual report on water clarity and suspended solids
80 | Glycol system freeze point where applicable
90 | Glycol system % of volume where applicable
100 | Inspect and record make up water meter reading
110 | Record all values, concentrations, control ranges for above in spreadsheet
120 | Chemical adjustments made, and recommendations for the heating system.
140 | Inspect and replace inline cartridge filters and O rings
150 | Provide and update all MSDS sheets on site
160 | Document the make-up water meter reading
170 | Blowdown if TDS level is high;
180 | Report Findings to Maintenance Supervisor
10 | Maintenance Personnel to collect water sample from HVAC system
20 | Submit the sample to a contractor who provides water testing
30 | Document the make-up water meter reading
40 | Determine & document the sulphite or Organic Phosphonate concentration of the water in the system
50 | Sulphite based treatments— must be 50-100 ppm SO3 (80– 160 ppm Na2SO3); do not blowdown if it is high;
60 | Determine & document the pH level of the water in the system (8.5-9.5 Ph);
70 | Add a pH buffer if it is low; blowdown if it is high;
80 | Determine & document the TDS (or conductivity) level of the water in the system, less than 2000 ppm or 2500 µS/cm;
90 | Blowdown if TDS level is high;
100 | Determine & document the visual appearance of the water, it must be clear & colourless;
110 | Replace the by-pass filter cartridge as needed (if applicable)
120 | Install iron & copper corrosion coupons for a 90 day interval once during the operational season.
130 | The Water Treatment Specialist may adjust the frequency depending on corrosion rate results.
140 | The iron corrosion rate must be less than 0.5 mpy, and the copper corrosion rate must be less than 0.2 mpy.
150 | Systems containing aluminum shall also have aluminum coupons installed for a 90 day interval once during the operational season,
160 | Aluminum corrosion rates must be less than1.0mpy.

## MECH-ET-A
MECH-ET | ANNUAL EXPANSION TANK INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Inspect For Leaks AT Welds, Valves and Baldders.
20 | Check Sight Glass, If Applicable.
30 | Check and Record Pressure: psi / Kpa
40 | Adjust To System Pressure If Required. Record New Pressure
50 | Inspect and check pressure redcuing valve for proper operation if equipped
60 | Findings Reported To Maintenance Supervisor

## PD-ST-A
PD-ST-A | ANNUALLY STORAGE TANK INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure the containment structure in satisfactory condition
30 | Check the drainage pipes/valves fit for continued service
40 | Check the integrity of tank foundation
50 | Check the tank supports in satisfactory condition
60 | Inspect the overflow pipe and properply connected to the drainage system
70 | Ensure the grounding strap secured and in good condition
80 | Check any paint failure. Repaint as needed
90 | Check for any corrosion or cracking. Repair as needed.
100 | Check flanged connection bolts tight and fully engaged with no signs of wear or corrosion
110 | Ensure the vents are free of obstructions
120 | Check the condition of wire mesh if equipped
130 | Test the function of liquid level sensing device to ensure proper operation
140 | Check the tank liquid level sensing device operate as required
150 | Check the overfill prevention devices in proper working condition
160 | Check the tank grounding lines in good condition
170 | Check the electrical wiring for control boxes/lights in good condition
180 | Clean the tank as needed. Adopt confined space / restricted area measures if applicable
190 | Findings Reported To Maintenance Supervisor

## SMP-W-01
SMP-W-01 | WEEKLY SUMP PIT INSPECTION (UNDERGROUND EFFLUENT TANK) - SOUTH
Sequence | Description
10 | Remove manhole cover with proper removal tool.
20 | Retrieve dip stick stored adjacent to the Vehicle Washbay Utility room
30 | Check the level in the tank
40 | if the level is =/> ¾ full call W&R Foreman for possible pumping-out
50 | Otherwise, call a vacuum truck vendor.
60 | Complete the W&R disposal form with the vendor disposing to the site

## SMP-M-01
SMP-M-01 | MONTHLY SUMP PIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Remove manhole cover with proper removal tools
20 | Check water level in the tank/sump pit and clear any silt or debris if required
30 | Test sump pump manually
40 | Add water treatment chemical as required
50 | Re-cover manhole and ensure it is properly secured
60 | Findings reported to Maintenance Supervisor

## STP-A-01
STP-A-01 | ANNUAL SEPTIC SYSTEM INSPECTION
Description
Call contrator prior to inspection to have tank cleaned out
Inspect pump in operation and comment on any abnormalities or leaks
30 | Inspect and clean pump body and motor ventilation
40 | Inspect pump coupling and alignment
50 | Lubricate motor bearings
60 | Inspect and clean associated pump strainer or filters
70 | Inspect electrical connections and mounting hardware
80 | Check Discharge Pressure +/- 10% of full flow, if applicable
90 | Check Suction Pressure +/- 10% of full flow, if applicable
100 | Check operation of high water float, if applicable
110 | Check operation of the effluent pump floats, if applicable
120 | Check general condition of tank - report any deficiencies
130 | Check condition of inlet sewer line - report any deficiencies
140 | Check condition of inlet baffle - report any deficiencies
150 | Check condition of outlet baffle - report any deficiencies
160 | Check effluent filter - replace or clean as required
170 | Check condition of compartment wall - report any deficiencies

## ST-W-01
ST-W-01 | WEEKLY SEPTIC TANK INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Remove septic tank cover - inspect area for leakage and other signs of failure
20 | Check that scum levels are MORE THAN 3" from the bottom of the outlet device
30 | Check that sludge layers are MORE THAN 12" from the bottom of the outlet device
40 | Test high level alarm or reset - if applicable
50 | Call contractor to clean septic tank if scum level or sludge layers are too high
60 | Replace septic cover and ensure it is properly secured
70 | Findings reported to Maintenance Supervisor

## SMP-A-03
SMP-A-03 | ANNUAL SEPTIC TANK CLEAN OUT
Sequence | Description
10 | Job Hazard Assessment Completed?
20 | Position the drain cleaning machine with associated accessories
30 | Select the proper length and size of vacuum hose
40 | Place pylons or barriers around the immediate work space.
50 | Engage the blower and begin to remove the waste from septic tank
60 | Checking the fluid levels in the septic tank
70 | Once the septic tank has been cleaned, remove the cleaning machine at once
80 | Cover the tank
90 | Make sure the waste has cleared the vacuum hose
100 | Shut down the blower, break apart the hoses and strap them down for travel
110 | Ensure that the work area is clear of all tools
120 | Fill out the proper disposal manifest
130 | Transport the waste to the City of Calgary Waste Disposal Site

## SMP-A-01
SMP-A-01 | ANNUAL SUMP PIT INSPECTION (UNDERGROUND EFFLUENT TANK)
Sequence | Description
10 | Inspect and clean underground effluent tank
20 | Report any observed issues to Facility Operations for approval on correction

## SMP-A-02
SMP-A-02 | ANNUAL SUMP PIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check electrical plug, cord and connection
20 | Activate float switch and check pump for proper operation
30 | Lubricate pump as required
40 | Inspect packing and tighten as required
50 | Clean out trash from sump
60 | Call a vacuum truck vendor as required
70 | Complete the W&R form with vendor
80 | Fill out maintenance checklist and report deficiencies
90 | Findings Reported To Maintenance Supervisor

## SMP-Q-01
SMP-Q-01 | QUARTERLY SUMP PIT CLEAN OUT
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check electrical plug, cord and connection
30 | Activate float switch and check pump for proper operation
40 | Lubricate pump as required
50 | Inspect packing and tighten as required
60 | Clean out trash from sump
70 | Call a vacuum truck vendor as required
80 | Complete the W&R form with vendor
90 | Fill out maintenance checklist and report deficiencies
100 | Findings Reported To Maintenance Supervisor

## GR-TRP-Q-01
TRP-GR-Q-01 | QUARTERLY GREASE TRAP INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | ***As per Waste Water BYLAW NUMBER 14M2012***
20 | Open the grease interceptor and suction off the top layer of grease
30 | Suction out the solids at the bottom of the interceptor
40 | Suction out any water
50 | Scrape & remove the baffles, thoroughly clean sides & bottom of the interceptor
60 | Ensure the inlet, outlet and air relief ports are clean and clear.
70 | Ensure that all internal components are working properly.
80 | Properly reinstall all seals, replacing any that are brittle or cracked.
90 | Securely fasten the cover & fill the grease interceptor with clean water.
100 | Hauler to dispose of all substances at licensed waste disposal facility.
110 | Hauler to record the sludge depth & free water depth during maintenance.
120 | Keep service records onsite for a minimum of two years.
130 | Findings reported to Maintenance Supervisor

## TRP-M-01
TRP-M-01 | MONTHLY TRAP AND DRAIN PRIMING INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect traps and floor drains
30 | Prime floor drains as necsry in washrm, Mech rm, Kitchens, Change rm, Janitorial
40 | Findings Reported To Maintenance Supervisor

## WS-Q-01
WS-Q-01 | QUARTERLY WATER SOFTENER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Ensure there is sufficient salt supply
20 | Check salt & brine system
30 | Check water meter & record reading
40 | Ensure the unit is running normally
50 | Record any problems
60 | Check and record hardness level
70 | Ensure salt is not bridging by using the long handle tools
80 | Findings reported to Maintenance Supervisor

## ET-A-01
ET-A-01 | ANNUAL EXPANSION TANK INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Inspect For Leaks AT Welds, Valves and Baldders.
20 | Check Sight Glass, If Applicable.
30 | Check and Record Pressure: psi / Kpa
40 | Adjust To System Pressure If Required. Record New Pressure
50 | Inspect and check pressure reducing valve for proper operation if equipped
60 | Findings Reported To Maintenance Supervisor

## MECH-S&RF-A
MECH-S&RF-A | ANNUAL SUPPLY AND RETRUN AIR FAN INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Remove Cover From Unit.
20 | Vacuum Unit Thoroughly.
30 | Check Unit Fastening Devices To Ensure All Are Secure.
40 | Check fan blades, fan housing and belt guard condition
50 | Replace belt if equipped
60 | Check fan driver and alignment. Repair or replace as needed
70 | Rotate Fan Wheel By Hand To Check Alignment Bearing Operation.
80 | Fan Wheel To Rotate Around Shaft, Without Binding Or Rubbing.
90 | Assess field serviceable bearings. Lubricate as needed
100 | Name Plate Data: Amps
150 | Name Plate Data: Volts
160 | Measured Data: Amps
170 | Measured Data: Volts
180 | Check motor contactor for pitting or damages. Repair or replace as needed
190 | Check integrity of flexible connections. Correct as needed
200 | Check Operating Lights. Replace Bulbs That Are Burnt Out.
210 | Check Proper Function in BMS if Equipped
220 | Findings Reported To Maintenance Supervisor

## HTRACE-S-02
HTRACE-S-02 | SEMI-ANNUAL HEAT TRACE INSPECTION (BULK WATER STATION)
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Visual inspect inside connection box for corrosion and moisture
30 | Check any damages for cracks or leaks in insulation
40 | Heat cable properly connected and grounded and insulated from connection box
50 | Check themostat for moisture, corrosion, set point and switch operation
60 | Carry out megger test if so required
70 | Ensure the system is "ON" in Fall and "OFF" in Spring
80 | Findings reported to Maintenance Supervisor

## PFCU-A-01
PFCU-A-01 | ANNUAL POWER FACTOR CORRECTION UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Instruction Manual For Automatic And Filtered
30 | Automatic Power Factor Correction Unit
40 | Clean the unit to remove any accumulation of dust
50 | Remove any moisture found inside the enclosure and take steps to
60 | prevent it from entering the enclosure
70 | Check that all wire connections are tight
80 | Visually inspect all components. Any wiring or component which shows signs of
90 | wear, discolouration, overheating, insulation breakdown or
100 | deterioration should be replaced
110 | Inspect capacitors for bulging or raised lid on the top. They will be taller
120 | than the other capacitors. Any capacitor with a bulging top should be replaced
130 | as the internal fuses will have cleared
140 | Check all fuses. The characteristics and ratings of replacement fuses should be
150 | the same as the original fuses. Cleared fuses could be the result of
160 | welded contactors or contactor chatter when closing
170 | Switch each step on and off using the controller
180 | Ensure the contactors open and close properly and are not
190 | chattering. Replace contactors if necessary
200 | Listen for excessive noise and vibrations. Loose bolts or
210 | high currents can cause noise and vibrations
220 | Ensure the power factor controller is functioning properly
230 | Findings Reported To Maintenance Supervisor

## DH-02
DH-02 | SEMI-ANNUALLY HOT WATER HEATER (TANKLESS) DESCALING
Sequence | Description
10 | Inspect inside of fuel pipe for any blockage or restrictions
20 | Remove and clean filter or replace if applicable
30 | Use pressurized air to remove dust from main burner, Heat Xchanger, & fan blade
40 | Check burner observation window for cracks or spillage of flue gases if applicab
50 | Observe burner flames during heater operation - S/B a steady blue
60 | Check condensate siphon for debris and clean if applicable
70 | Disconnect electrical power to the water heater.
80 | Close the shutoff valves on both the hot water and cold water lines
90 | Connect pump outlet hose to the cold water line at service valve
100 | Connect drain hose to service valve
110 | Pour approximately 4 gallons of virgin, food grade, white vinegar or citric acid
120 | Place the drain hose and the hose to the pump inlet into the cleaning solution.
130 | Open both service valves on the hot water and cold water lines.
140 | Pump the solution to circulate through the water heater for 5 min.
150 | Turn off the pump.
160 | Rinse the cleaning solution from the water heater
170 | Allow water to flow through the water heater for 5 minutes
180 | Remove the in-line filter at the cold water inlet and clean out any residue
190 | Restore electrical power to the water heater.

## EL-M-02
EL-M-02 | MONTHLY EMERGENCY LIGHTING INSPECTION (Rev.1)
Sequence | Description
10 | Pilot Light Operating
20 | Activate the Battery Unit(s) either by the Test Switch/button
30 | Or unplugging the power cord from the receptacle, whichever is most convenient
40 | **ELECTRICIAN REQUIRED IF YOU MUST FLIP THE BREAKER TO TEST THE DEVICE***
50 | Observe the operation of the unit for 30 seconds.
60 | Verify that all DC lamps in the area served by the unit and exit signs are lit.
70 | Restore AC power to the Battery Unit(s).
80 | Document the test results.

## SHP-S-01
SHP-S-01 | SEMI-ANNUAL SHORING POST INSPECTION
Sequence | Description | Type
10 | Pre Job Hazard Assessment Completed? | Question (Yes/No)
20 | Coordinate with engineering and/or professional firms to conduct inspection | Checklist Item
30 | based on regulatory requirements and industrial best practices | Checklist Item
40 | Review engineering report with City Corporate Engineering and stakeholders | Checklist Item
50 | Present observations to stakeholders & take relative actions where applicable | Checklist Item
60 | Findings Reported To Facility Operation Supervisor | Question (Yes/No)

## ROOF-S-01
ROOF-S-01 | SEMI-ANNUAL ROOFING INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Remove ALL debris from roof / DO NOT throw debris onto ground
30 | Inspect roof drains - Remove all leaves, debris, etc / Ensure drain has cover
40 | if not replace ASAP / Draincovers should be metal
50 | Inspect roof drains for any ponding water. If water, cleaned out drains ASAP
60 | Inspect roof flashings - Inspect caulking for deterioration
70 | If caulking is damaged, and area is minor, clean surface & install new caulking
80 | Report area of replaced caulking
90 | If damaged caulking area is too large to repair, report all areas to be repaired
100 | Inspect downspouts & eavestroughs
110 | Remove all debris & make sure that downspouts & eaves are secured & sealed
120 | Inspect all gum boxes as required. Gum boxes will be found where
130 | electrical conduit wires have penetrated the roof system, near &/or around RTU
140 | Fill gum cups wth Soprema Aluminized gum cup filler. Report all repair locations
150 | Check for exposed insulation - Cover with ballast (rocks)
160 | Inspect roof hatch for tight seal/Hatch should open & close easily
170 | & be locked when not being used (hatch open/closes easily - yes/no)
180 | Check roof ladders are secured to building & have cage (cage on ladder - yes/no)
190 | Check for ponding water, blisters, ridges / If found, list areas
200 | Note & report interior location of any leaks
210 | Findings Reported to Maintenance Supervisor

## STRU-A-01
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Coordinate with engineering and/or professional firms to conduct inspection
30 | based on regulatory requirements and industrial best practices
40 | Review engineering report with City Corporate Engineering and stakeholders
50 | Present observations to stakeholders & take relative actions where applicable
60 | Findings Reported To District Co-Ordinator & City Corporate Engineering

## DH-A-01
DH-A-01 | ANNUALLY DOMESTIC HOT WATER HEATER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Unit, Piping, Valves, Welds And Connections For Leaks
30 | Check Firing Cond Flame Through Burner Access Door, Circle Colour: Blue Yellow
40 | If Flame Is Yellow, Adjust Combustion Air Setting As Per Manufacturer'S Recom
50 | Inspect Burner Combustion Chamber Report Signs Corrosion Or Deterioration
60 | Examine Venting System For Leakage-Report, Record Deterioration Or Corrosion
70 | Check And Record DHW Discharge Temperature : Actual Temp Celsius
80 | Check And Record DHW Setpoint (If Applicable) : Setpoint Temp Celsius
90 | Check the operation of the thermostat
100 | Ensure the flow of combustion and ventilation air MUST NOT be restricted
110 | Clear the combustion air openings of any dirt, dust, or other restrictions
120 | Inspect the main & pilot burner flames to determine they are burning properly
130 | If sooting or other burner anomalies are evident, shut down
140 | the water heater by turning off the gas per the instructions
150 | Check for damaged components &/or joints not sealed. Repair or replace as needed
160 | Remove the inner door and main burner assembly to clean orifices
170 | and related parts of any dirt or other foreign material.
180 | Inspect burner ports for obstruct°/debris & clean with a wire brush as needed
190 | Clean combust° chamber from scale deposit/debris if nec. with wire brush/vacuum
200 | Check temp./pressure relief valve to insure the valve is not encrusted with lime
210 | Lift the lever at the top of the valve several times until the valve seats
220 | properly without leaking and operates freely
230 | Inspect the anode rod and replaced when necessary to extend tank life
240 | Drain off a gallon of water to remove silt and sediment
250 | Measure Amperage When Heater Is In Operation: (For Electric Units Only) :
260 | Equipment Specification : __________Amps
270 | Measured : __________Amps
280 | Use Portable Co Detector To Sniff Boilers And Associated Ductwork For Leaks
290 | CO Readings : __________ppm
300 | Inspect All Intakes, Exhaust Flanges, Ductwork, Connections. Tighten as needed
310 | Findings Reported To Maintenance Supervisor

## VT-BW-01
VT-BW-01 | BI-WEEKLY ELECTRICAL VAULT INSPECTION
Sequence | Description
10 | Inspect equipment
20 | Ensure cleanliness of area
30 | Ensure lighting levels are adequate

## MECH-DP-S
MECH-DP | SEMI-ANNUALLY CONTROL DAMPERS (HVAC) INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Observe damper motors and actuators through an operating cycle to check for defects or binding.
30 | All mounting bolts must be securely fastened.
40 | Linkages from actuators should be adjusted to insure blades of damper fully open or close within the stroke or travel of the actuator arm.
50 | Blades should be checked in closed position to be sure all close tightly. Adjusts for damper linkage as needed
60 | Remove all dirts and soot lint around operating parts.
70 | Check pins, straps, bushings (bearings) for wear, rust or corrosion. Replace as needed.
80 | Lubricate all mechanisms and moving parts.
90 | Check caulking of damper frames are tight to ductwork, repaired as needed.
100 | Close all fresh air dampers before winter and resume normal in spring.
110 | Check the proper operation of dampers in BMS if equipped.
120 | Check the function of all interlocking devices.
130 | Findings Reported To Maintenance Supervisor

## AHU-A-01
AHU-A-01 | ANNUAL AIR HANDLING UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Inspect And Clean All Compartments, if any sign of corrosion and apply touch up rustproof painting
30 | Check All Unit Component Fastening Devices Are Secure
40 | Inspect Rubber Gaskets Around Access Doors, Door handles, latches for proper operation
50 | Replace Belts
60 | Check Tension And Condition Of Belts And Pulley Alignment and its protective guard
70 | Replace All Interior Filters and Check differential pressure gauge in filter section
80 | Clean Exterior Metal Pre-Filter
90 | Lubricate Motors And Fan Bearings
100 | Check Blower Alignment, Bearing Operation, fan housing, shaft, isolator, Inlet vanes for damage, loose, dirt and debris
110 | Check Dampers And Linkages For Damage And Wear
120 | Check Operation Of All Safety Controls (High & Low Temp, High&Low Static Pres Cut-out, Air Flow) and Control Valves
130 | Conduct visual check to all water pipes, drainage for leakage and make good minor insulation damage
140 | Inspect Heat Exchanger for proper operation
150 | Check Refrigerant Charge (if applicable)
160 | Clean Condenser And Evaporator / (Cooling & Heating) Coil
170 | Inspect Condenser And Evaporator / (Cooling & Heating) Coil
180 | Comb All Damaged Fins for coils
190 | Perform Refrigerant Leak Check (if applicable)
200 | Inspect Refrigerant Lines And Evidence Of Oil Leaks (if applicable)
210 | Check Compressor Oil Level (if applicable)
220 | Check Refrigerant Operating Temperature And Pressures (if applicable)
230 | Check Condenser Fans And Tighten Set Screws (if applicable)
240 | Inspect And Clean All Condensate Pans And Clean Condensate Drains
250 | Check Electrical Terminations Are Secure And All Fuses Are Intact
260 | Inspect And Clean Contactors and Motor starter Panel
270 | Measure And Record Motor Amperages - Supply Air Fan Motor Amp
280 | Measure And Record Motor Voltage - Supply Air Fan Motor Volt
290 | Measure And Record Motor Amperages - Return Air Fan Motor Amp
300 | Measure And Record Motor Voltage - Return Air Fan Motor Volt
310 | Measure And Record Motor Amperages - Exhaust Fan Motor (if applicable) Amp
320 | Measure And Record Motor Voltages - Exhaust Air Fan Motor Volts (if applicable) Volt
330 | Measure And Record Motor Amperages - Desiccant Wheel Motor (if applicable) Amp
340 | Measure And Record Motor Voltages - Desiccant Wheel Motor (if applicable) Volt
350 | Measure And Record Motor Amperages - Compressor Motor (if applicable) Amp
360 | Measure And Record Motor Voltages - Compressor Motor (if applicable) Volt
370 | Measure And Record Motor Amperages - Condenser Fan Motor (if applicable) Amp
380 | Measure And Record Motor Voltages - Condenser Fan Motor (if applicable) volt
390 | Measure And Record Motor Amperages - Evaporator Motor (if applicable) Amp
400 | Measure And Record Motor Voltages - Evaporator Motor (if applicable) volt
410 | Check operation of temperature switch and humidistat if applicable
420 | Inspect And Clean Dehumidifier's Desiccant Wheel (if applicable)
430 | Inspect Chain And/Or Belt Drive On Desiccant Wheel Motor (if applicable)
440 | Findings Reported To Facility Supervisor And Facility Operations Coordinator

## AHU-Q-01
AHU-Q-01 | QUARTERLY AIR HANLDING UNIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Inspect And Clean All Compartments
20 | If any sign of corrosion, apply touch up rustproof painting
30 | Check All Unit Component Fastening Devices Are Secure
40 | Inspect Rubber Gaskets Around Access Doors,handles,latches for proper operation
50 | Inspect and Check Belts Condition
60 | Check Tension And Condition Of Belts And Pulley Alignment and Protective Guard
70 | Replace Pre Filters & Final Filters as needed
80 | Check differential pressure gauge in filter section
90 | Clean Exterior Metal Pre-Filter
100 | Lubricate Motors And Fan Bearings
110 | Check Blower Alignment and Bearing Operation for Damage, Loose Dirt and Debris
120 | Check Fan Housing, Shaft, Isolator, Inlet Vanes For Damage, Loose Dirt/Debris
130 | Check Dampers And Linkages For Damage And Wear
140 | Check Operation Of All Safety Controls and Control Valves including:
150 | High & Low Temp, High & Low Static Pressure Cut-out, Air Flow
160 | Conduct visual check to all water pipes, drainage for leakage
170 | Repair minor insulation damage
180 | Check Refrigerant Charge (if applicable)
190 | Inspect Condenser And Evaporator / (Cooling & Heating) Coil
200 | Comb All Damaged Fins for Coils
210 | Perform Refrigerant Leak Check (if applicable)
220 | Inspect Refrigerant Lines & Evidence Of Oil Leaks (if applicable)
230 | Check Compressor Oil Level (if applicable)
240 | Check Refrigerant Operating Temperature And Pressures (if applicable)
250 | Check Refrigerant Operating Temperature And Pressures (if applicable)
260 | Check Condenser Fans And Tighten Set Screws (if applicable)
270 | Inspect And Clean All Condensate Pans And Clean Condensate Drains
280 | Findings Reported To Maintenance Supervisor

## AHU-M-01
AHU-M-01 | MONTHLY AIR HANDLING UNIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Check controls and unit for proper operation.
20 | Check for unusual noise or vibration.
30 | Check tension, condition and alignment of belts, adjust as necessary.
40 | Clean coils, evaporator drain pan, blower, motor and drain piping, as required.
50 | Lubricate shaft and motor bearings. (if applicable)
60 | Replace air filters. (if required)
70 | Inspect exterior piping and valves for leaks; tighten connections as required.
80 | Clean area around equipment.
90 | Fill out maintenance checklist and report deficiencies.
100 | Inspect exterior door covers to ensure locked.
110 | Use heatgun to inspect proper operational temp of electric motors, as required.
120 | Findings Reported To Maintenance Supervisor

## FA-M-01
FA-03 | MONTHLY FIRE ALARM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per CAN/ULC-S536 Standard for monthly inpsection
30 | To inspect the system trouble signal indicator "OFF"
40 | To inspect the power indication lamp "ON"
50 | ***FIRE ALARM***
60 | Location of alarm initiating devices
70 | Operation and inspection of one initiating fiedl device - rotational
80 | Alert / Alarm signal confirmed - rotational
90 | Tested device annunciates correctly
100 | Operation of common audible and visual trouble signal confirmed
110 | ***BATTERY***
120 | Terminal cleaned and lubricated
130 | Terminal clamps secure
140 | Electrolyte level and specifc gravity to specification
150 | ***VOICE COMMUNICATION***
160 | Location of emergency telephone
170 | One emergency telephone for two-way communication and indication - rotational
180 | Location of voice page zone
190 | Test voice paging to one zone - rotational
200 | Findings Reported To Maintenance Supervisor
Existing task in EAM
10 | (Fire Alarm; Can/Ulc-S536 (Check If Applicable)
20 | Operate One Initiating Device Or Manual Station (On A Rotational Basis)
30 | Device Address
40 | Verify Alert And Or Alarm Signal (On At Least One Zone On A Rotational Basis)
50 | Location
60 | Verify Device Annunciation On The Control Panel
70 | Verify Alarm Transmission To The Monitoring Station
80 | Test A Fire Fighters Phone (On A Rotational Basis).
90 | Verify Two Way Communication
100 | Location
110 | Test The Voice Paging (On At Least One Zone On A Rotational Basis)
120 | Location
130 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
140 | Pre Job Hazard Assessment Completed?

## FI-PU-A-01
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NFPA 25 Standard - Chapter 8 (8.1-8.3) requirement for inspection
30 | ***General Inspection***
40 | Inspect cable / wire insulation 8.3.6.4
50 | Inspect engine crankcase breather 8.1.1.2.12
60 | Inspect exhuast system and drain condensate trap 8.1.1.2.13
70 | Inspect flexible hoses and connections 8.1.1.2.11
80 | Inspect fuel tank vents and overflow if equipped 8.1.1.2.10
90 | Inspect shaft movement while running 8.1.1.2.1
100 | Inspect the suction screen and clear of any debris 8.3.3.12
110 | ***Test***
120 | Test diesel fuel for any degradation as per ASTM D975. Correct as needed 8.3.4
130 | Conduct annual flow testing and record pump performance 8.3.2 & 8.3.3
140 | Activate fire alarm circuits including local and remote alarm indicating devices
150 | Test backup electronic module (ECM) with associated sensors if equipped 8.3.3.13
160 | Test the main relief valve 8.3.3.8
170 | Test the function overcurrent protective devices when triggering the ATS 8.3.3.9
180 | Check fuel tank, float switches and supervisory signal if equipped 8.1.1.2.7
190 | Check supevisory signal circuitry for high cooling water temperature if equipped
200 | ***Maintenance***
210 | Check battery condition and clean the terminals of any corrosion 8.1.1.2.15
220 | Replace circulation water filter if equipped 8.1.1.2.20
230 | Check all control and power wiring connection 8.1.1.2.16
240 | Change lubrication oil in engines 8.1.1.2.17
250 | Change lubrication oil filter 8.1.1.2.18
260 | Check fuel tanks for water and foreign materials 8.1.1.2.9
270 | Measure back pressure on the engine turbos if equipped 8.1.1.2.14
280 | Inspect the accuracy of pressure gauages and sensors 8.1.1.2.21
290 | Grease pump and motor bearings and couplings 8.1.1.2.3
300 | Check the condition of sacrificial anodes, replace as needed 8.1.1.2.19
310 | Record any deficiencies and submission of test report
320 | ***Pump System Procedure***(While the pump is running) - 8.3.2.9
330 | Record the system starting pressure from the pressure switch or pressure transdu
340 | Record the system suction and discharge pressure gauge readings
350 | Inspect the pump packing glands for slight discharge
360 | Adjust gland nuts if necessary
370 | Inspect for unusual noise or vibration
380 | Inspect packing boxes, bearings, or pump casing for overheating
390 | Record pressure switch or transducer reading and compare to pump discharge gauge
400 | Record highest and lowest current pressure if use electronic pressure sensor
410 | Check the circulation relief valve for operation to discharge water
420 | ***Electrical System Procedure***(While the pump is running)
430 | Observe the time for motor to accelerate to full speed
440 | Record the time controller is on first step (for reduced voltage/current start)
450 | Record the time pump runs after starting (for automatic stop controllers)
460 | ***Diesel Engine System Procedure***(While the pump is running) - If applicable
470 | Observe the time for engine to crank
480 | Observe the time for engine to reach running speed
490 | Observe the engine oil pressure gauge, speed indicator, water and oil temperatur
500 | Record any abnormalities
510 | Inspect the heat exchanger for cooling waterflow
520 | Findings reported to Maintenance Supervisor

## FI-PU-M-01
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NFPA 25 Standard - Chapter 8 (8.2.2 & 8.3.2.9) requirement for inspection
30 | **Pump house condition***
40 | Not <4.0 Deg.C for electric motor or diesel engine pump with engine heaters
50 | Not less than 21.0 Deg.C with disel pump without enginer heaters
60 | Ventilation louvres are free to operate
70 | Excessive water does not collect on floor
80 | Coupling guard in place
90 | ***Pump system condition***
100 | Pump suction and discharge and bypass valve are fully open
110 | Piping is free of leaks
120 | Suction line pressure gauge reading is within acceptable range.
130 | System line pressure gauge reading is within acceptable range.
140 | Suction reservoir has the required water level.
150 | Wet pit suction screens are unobstructed and in place.
160 | Waterflow test valves are in the closed position,
170 | The hose connection valve is closed, and the line to test valves is free of wate
180 | Record the pump starting pressure from pressure switch under running 8.3.2.9
190 | Recod the system suction and discharge gauge readings (PSI) 8.3.2.9
200 | Inspect the pump packing glands for slight discharge 8.3.2.9
210 | Adjust glands nuts if needed 8.3.2.9
220 | Inspect for abnormal noise or vibration 8.3.2.9
230 | Inspect packing box, bearings or pump casing for overheating 8.3.2.9
240 | Record pressure switch reading and compare to the pump discharge gauge 8.3.2.9
250 | Check the circulation relief valve for operation to discharge water 8.3.2.9
260 | ***Electrical system conditions***
270 | Controller pilot light (power on) is illuminated.
280 | Transfer switch normal pilot light is illuminated.
290 | Isolating switch is closed — standby (emergency) source.
300 | Reverse phase alarm pilot light is off, or normal phase rotation pilot light is
310 | Oil level in vertical motor sight glass is within acceptable range.
320 | Power to pressure maintenance (jockey) pump is provided.
330 | Observe the time for motor to accelerate to full speed 8.3.2.9
340 | Record the time pump runs after starting 8.3.2.9
345 | Conduct no-flow test for electric motor–driven pump
350 | ***Diesel engine system conditions***(If applicable)
360 | Fuel tank is at least two-thirds full.
370 | Controller selector switch is in auto position.
380 | Batteries’ voltage readings are within acceptable range.
390 | Batteries’ charging current readings are within acceptable range.
400 | Batteries’ pilot lights are on or battery failure pilot lights are off.
410 | All alarm pilot lights are off.
420 | Engine running time meter is reading.
430 | Oil level in right angle gear drive is within acceptable range.
440 | Crankcase oil level is within acceptable range.
450 | Cooling water level is within acceptable range.
460 | Electrolyte level in batteries is within acceptable range.
470 | Battery terminals are free from corrosion.
480 | Water-jacket heater is operating.
490 | Conduct no-flow test for diesel engine-driven pump (if applicable)
500 | Observe the time for engine to crank 8.3.2.9
510 | Observe the tie for engine to reach running speed 8.3.2.9
520 | Observe the engine oil pressure gauge, speed indicator 8.3.2.9
530 | Record any abnormailities 8.3.2.9
540 | Inspect the heat exchanger for cooling waterflow 8.3.2.9

## AED-B-01
AED-B-01 | BIENNIAL AUTOMATED EXTERNAL DEFIBRILLATOR INSPECTION
Sequence | Description | Type | Equipment Level | Out of Service
10 | Perform inspection and safety checks according to Manufacturer's specification | Checklist Item | Header Equipment | NO
20 | Replace battery pack when required | Checklist Item | Header Equipment | NO
30 | Replace electrodes pack when required | Checklist Item | Header Equipment | NO
40 | Perform Software Updates at the time of inspection | Checklist Item | Header Equipment | NO
50 | Report for any deficiency found and recommend action if needed | Checklist Item | Header Equipment | NO

## EL-M-04
EL-M-04 | Monthly Emergency Lighting Inspection
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Pilot Light Operating
30 | Activate the Battery Unit(s) either by the Test Switch/button
40 | Or unplugging the power cord from the receptacle, whichever is most convenient
50 | **ELECTRICIAN REQUIRED IF YOU MUST FLIP THE BREAKER TO TEST THE DEVICE**
60 | Observe the operation of the unit for 30 seconds.
70 | If not standalone unit, verify that all DC lamps in the area served by the unit
80 | And exit sign are lit
90 | Restore AC power to the Battery Unit(s)
100 | Document the test results and report the deficiency to maintenance supervisor
110 | Or create Service Request

## EL-01
EL-01 | Annual Emergency Lighting Inspection
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Before Testing, Make The Following Checks And Record Observations:
20 | Charge Light Status.
30 | Charge Light Operation.
40 | Check Electrical Connections
50 | Secure Mounting Hardware
60 | Clean And Dry Lamp Lens.
70 | Lamp And Socket Connection.
80 | Disconnect Electrical Power At Electrical Panel.
90 | Verify Each Light For Correct Operation. Record The Status Of Each Light.
100 | While Emergency Lights Are On, Check Direction Of Lamps.
110 | Verify Replacement Date Of Batteries And Record.
120 | For Wet Battery Units: Top-Up Electrolyte With Distilled Water Only And Record.
130 | Findings Reported To Maintenance Supervisor
140 | Above task plan is the minimum requirement to follow
150 | Contractor is responsible to comply with all update and applicable codes as req

## FSS-M-01
FSS-M-01 | Monthly Fire Sprinkler System Inspection
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Code NFPA 25 - 2017 For Monthly Inspection
30 | ***GAUGE AND CONTROL VALVE***
40 | Gauge is operable and not physically damaged.
50 | Gauges monitoring air or nitrogen pressure are being maintained
60 | Gauge in good condition and normal water pressure maintained. Pressure:_____ PSI
70 | Valves in normal open or close position
80 | Sealed, locked, or supervised
90 | Accessible
100 | Post Indicate Valve (PIV) with correct wrenches
110 | Free from external leaks
120 | Provided with applicable identification
130 | ***Backflow Prevention Assemblies***
140 | Inspect reduced pressure assemblies and detector
150 | Ensure differential-sensing valve not discharging
160 | *Dry / Deluge Pipe Valves, Waterflow Devices, Check Valves (if applicable)*
170 | Valves is free from physical damage
180 | Trim valve(s) in normal open or closed position
190 | Valve seat is not leaking
200 | Electrical components are in service
210 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM
Sequence | Description
10 | Sprinkler; (Nfpa-25): Inspect Control Valves, Supervisory And Alarm Switches
20 | Sprinkler; (Nfpa-25): Ensure All Supervised Valves Are Open
30 | Sprinkler; (Nfpa-25): Record Pressures On All Gauges
40 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
50 | Pre Job Hazard Assessment Completed?

## SAFETY-FPS-LSR
SAFETY-FPS-LSR-A-01 | ANNUALLY LIFE SAFETY ROPE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Meet CSA Standard CAN/CSA-Z259.2.1-98 (R2004), Fall Arresters, Vertical Lifelines, and Rails
30 | Approved by NFPA Standard 1983, Standard on Life Safety Rope and Equipment for Emergency Services
40 | Must be inspected by worker before it is used on each shift
50 | Keep free from substance and condition to avoid deterioration of equipment
60 | Re-certified as specified by manufacturer if needed
70 | Life safety rope extends downward to within 1.2 metres of ground level
80 | Free of knots or splices throughout the travel portion
90 | Effective protected to prevent abrasion by sharp or rough edges
100 | Material appropriate to hazard and able to withstand adverse effect
110 | Minimizes the harzard of swinging and limits the swing drop distance to 1.2 metres if worker falls
120 | Findings Reported To Maintenance Supervisor

## SAFETY-FPS-HOOKS
SAFETY-FPS-HOOKS-A | ANNUALLY CARBINER AND SNAP HOOKS INSPECTION
Seqience | Description
10 | Pre Job Hazard Assessment Completed?
20 | Must be inspected by worker before it is used on each shift
30 | Keep free from substance and condition to avoid deterioration of equipment
40 | Re-certified as specified by manufacturer if needed
50 | Carabiner or snap hook is self closing and self-locking
60 | Opened by at least two consecutive deliberate actions
70 | Marked with its breaking strength in major axis
80 | Marked with the name or trademark of manufacturer
90 | Findings Reported To Maintenance Supervisor

## EL-SA-A
EL-SA-A | ANNUALLY SURGE ARRESTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Visually inspect the surge arrestor devices for damage, surface contamination
50 | Verify the integrity of the bottom ground connection
60 | Verify the ground lead is individually attached to a ground bus or ground electrode
70 | Inspect stroke counter is correctly mounted and electrically connected if equipped
80 | Verify the device support and alignment while cleaning
90 | Comply with Canadian Electrical Code, Part I, Section 1o for high voltage outdoor surge protecive device
100 | Verify ratings of surge arrestor meets design requirement
110 | ***Electrical Testing***
120 | Perform insulation reistance test from phase terminal to case and verify the manufacturer's data
130 | Measure grounding connection resistance
140 | Inspect bolted connections
150 | Findings Reported To Maintenance Supervisor

## EL-LP-A
EL-LP-A | ANNUALLY LIGHTNING PROTECTION SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | Physically pulling / tugging on conductors to ensure soundness and continuity
40 | Visual inspect the air terminals, ring, down conductors, bonding conductors and ground electrodes
50 | Ensure the system is in good repair
60 | No loose connections
70 | No part of system has been weakened due to corrosion or vibration
80 | All conductors, ground wires and terminal are intact
90 | No physical damages for equipment
100 | Surge protective device are in good condition
110 | Any expansion or additions to the facility are adequately protected and connected to existing system
120 | Findings Reported To Maintenance Supervisor

## EL-SSS-A
EL-SSS-A | ANNUALLY SURVEILLANCE AND SECURITY SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | Visual inspection and cleaning of all security system control cabinets and camera equipment
40 | Carry out alarm circuit functional tests
50 | Vehicle barrier and gate control functional tests
60 | Key card control circuit functional tests
70 | Camera and monitor control circuit functional tests
80 | Security system power supplies and UPS system functional tests
90 | Findings Reported To Maintenance Supervisor

## EL-PA-A
EL-PA-A | ANNUALLY PUBLIC ADDRESS SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | Perform functional and security tests
40 | Verify that no diagnostic failures are indicated
50 | Review the event log file, verify that events are correctly logged
60 | Review the system diagnostic log file, correct deficiencies notes in log file
70 | Test system activation for specific zones
80 | Verify field components perform in proper operation
90 | Verify the system will operate during power suspension and verify functionality
100 | Perform a visual inspection of all components
110 | Verify enclosure integrity is not compromised
120 | Perform a visual inspection of antennas
130 | Verify that connections are solid and no corrosion
140 | Perform a visual inspection and transceivers and verify proper operation
150 | Verify the alarm status on the central console
160 | Verify ac power failure alarm and the battery voltage under load
170 | Test the most recent software system backup
180 | Test mass notification system for evacuation purposes
190 | Findings Reported To Maintenance Supervisor

## EL-SCADA-A
EL-SCADA-A | ANNUALLY SUPERVISORY CONTROL AND DATA ACQUISITION SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | Produce a report on system performance and any problems encountered
40 | Conduct functional checks of equipment to confirm operability
50 | Visual check to each remote terminal unit (RTU)
60 | Clean each site of dust and vermin
70 | Carry out telemetry operations with the central and master sites
80 | Make a backup of all system programs and configuration
90 | Set up and synchronize time and date on all RTUs
100 | Carry out a complete and thorough audit of the entire system
110 | Test and measure the main operating parameters including voltages, currents, frequencies, input, outputs, levels and noises
120 | Submission of comprehensive report from supplier or contractor
130 | Calibrate the system as per manufacturer's recommendations
140 | Test all management functions for operating system such as Microsoft, Apple, Linus or UNIX
150 | Findings Reported To Maintenance Supervisor

## CE-CCOMM-A
CE-CCOMM-A | ANNUALLY CRITICAL COMMUNICATION SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect the physical and mechanical condition of equipment and wiring
50 | Inspect the physical condition of all cases, covers and accessories
60 | Verify target or LED / LCD operation and reset
70 | Clean the components
80 | Verify settings / configurations as per engineered settings
90 | Verify appropriate grounding equipment and circuits
100 | Download events, maintenance / statistical data prior to any tests
110 | Check tightness of all connections
120 | Verify correct data and time are displayed on the device
130 | Check for applicable firmware updates and product recalls
140 | ***Electrical Testing***
150 | Perform metering tests on all analog inputs
160 | Verify metering valus on HMI and at remote terminals
170 | Verify operation of all enabled digital inputs
180 | Verify operation of all digital outputs by operating the controlled device
190 | Verify all communication links are operational
200 | Verify operation of all internal logic functions used in the protective and control system
210 | Findings Reported To Maintenance Supervisor

## UPS-A-01
UPS-A-01 | ANNUALLY UNINTERRUPTED POWER SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect the UPS system cabinet, mounts, anchorage, clearances, ventilation and grounding are in good condition
50 | Observe and note any alarms/events
60 | Verify UPS settings match design
70 | Test static transfer from inverter to bypass and back
80 | Test all mechanical and electrical interlock systems
90 | Verify fuse size match design
100 | Coordinate with BU personnel for scheduling purposes
110 | Assist the vendor on the site if needed
120 | Visually inspect batteries, UPS and associated equipment for any signs of damage
130 | Verify that all fans are operational.
140 | Check air filters if equipped
150 | Inspect internal components for signs of damage, overheating or other problems.
160 | Check for corrosion of battery connections and record findings
170 | Check condition of battery hardware, cables.
180 | Clean unit
190 | Note any discrepancies found.
200 | Place UPS on line and note proper operation and load level.
210 | ***Electrical test***
220 | Record all meter readings, alarms, stored data, etc., available from the UPS dis
230 | Measure system voltage from positive to ground and negative to ground
240 | Function UPS alarm
250 | Inspect bolted connections
260 | Provide written or electronic report.
270 | Findings Reported To Maintenance Supervisor
Existing task in EAM | UPS-A-01
Sequence | Description
10 | Please contact the vendor to perform the annual PM
20 | Coordinate with Waste and Recycling personnel for scheduling purposes
30 | Assist the vendor on the site if needed
40 | Visually inspect batteries, UPS and associated equipment for any signs of damage
50 | Verify that all fans are operational.
60 | Record all meter readings, alarms, stored data, etc., available from the UPS dis
70 | Check air filters if any
80 | Place UPS in bypass
90 | inspect internal components for signs of damage, overheating or other problems.
100 | Check for corrosion of battery connections and record findings
110 | Check condition of battery hardware, cables.
120 | Clean unit
130 | Note any discrepancies found.
140 | Place UPS on line and note proper operation and load level.
150 | Provide written or electronic report.

## EL-CAP-A
EL-CAP-A | ANNUALLY CAPACITOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Visually inspect capacity for damage, surface contamination
50 | Verify the integrity of the ground connection
60 | Clean bushings / insulators
70 | Verify rating and configuration of capacitors meet design requirement
80 | ***Electrical Testing***
90 | Perform insulation reistance test from phase terminal to case and verify the manufacturer's data
100 | Measure resistance of internal discharge resistor
110 | Inspect bolted connections
120 | Findings Reported To Maintenance Supervisor

## VFD-01
EL-VFD-A | ANNUALLY VARIABLE FREQUENCY DRIVE INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | ***Visual and mechanical test***
20 | Inspect anchorage and grounding
30 | Vacuum Dust And Dirt From Heat Sink Fins
40 | Clean Or Replace Intake Air Filters As Conditions Require
50 | Check Ventilation Fans For Proper Operation And Clean As Needed.
60 | Confirm Vfd'S Ventilation Clearances Have Not Been Obstructed
70 | If Possible, Perform An Ir Thermal Scan Of The Vfd'S Power Input Output.
80 | Confirm The Vfd Doors And Covers Are In Place And Properly Closed
90 | ***Electrical testing***
100 | Check Electrical Connections And Re-Torque As Needed.
110 | Check Line Voltage
120 | Check Motor & Output Phase Balance
130 | Inspect Dc Buss Capacitors (Older Drives)
140 | Record The Vfd'S Parameter Settings Using Mct-10
150 | Test and replace ac and dc electrolytic capacitor until end of their life
160 | Inspect bolted connections
170 | Findings Reported To Maintenance Supervisor
Existing task in EAM | VFD-01
Sequence | Description
10 | Vacuum Dust And Dirt From Heat Sink Fins
20 | Clean Or Replace Intake Air Filters As Conditions Require
30 | Check Ventilation Fans For Proper Operation And Clean As Needed.
40 | Confirm Vfd'S Ventilation Clearances Have Not Been Obstructed
50 | Check Electrical Connections And Re-Torque As Needed.
60 | If Possible, Perform An Ir Thermal Scan Of The Vfd'S Power Input Output.
60 | Check Line Voltage
70 | Check Motor & Output Phase Balance
80 | Inspect Dc Buss Capacitors (Older Drives)
90 | Record The Vfd'S Parameter Settings Using Mct-10
100 | Confirm The Vfd Doors And Covers Are In Place And Properly Closed
110 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
120 | Pre Job Hazard Assessment Completed?

## VFD-S-01
VFD-S-01 | SEMI-ANNUALLY VRAIABLE FREQUENCY DRIVE INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Vacuum Dust And Dirt From Heat Sink Fins
20 | Clean Or Replace Intake Air Filters As Conditions Require
30 | Check Ventilation Fans For Proper Operation And Clean As Needed.
40 | Confirm VFD'S Ventilation Clearances Have Not Been Obstructed
50 | Confirm The VFD Doors And Covers Are In Place And Properly Closed
60 | Inspect push buttons, connectors and switches
70 | Check for faulty grounding
80 | Check input drive voltages and current level for motors
90 | Check for voltage and current anomalies
100 | Findings reported to Maintenance Supervisor

## OHD-A-01
OHD-A-01 | ANNUALLY OVERHEAD DOOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Disconnect Door From Operator, Check And Adjust Balance
30 | Check Drums And Cables, Adjust If Necessary.
40 | Check Set Screws On Springs And Drums.
50 | Inspect all nuts, threaded rods and anchors. Tighen any loose hardwares.
60 | Check Cross Bar Latch, Adjust If Necessary.
70 | Check conditon of Vertical And Horizontal Guides.
80 | Lubricate Hinges And Guide Rollers.
90 | Check And Lubricate Shaft Bearings and Springs.
100 | Check Hand Chain Gears For Alignment And Lubricate Where Necessary.
110 | Check And Adjust Stops To Ensure Easy Operation.
120 | Check And Lubricate Idler Sheaves And Adjust Where Necessary.
130 | Check Counterweight Cables And System.
140 | Inspect the condition of door panel, side column, reversing edge and photo eyes.
150 | Check OHD proper operation. See if smoothly/efficiently. Check abnorm noise/Vibr
160 | Check all electrical connections inside the control panel are tightly secured.
170 | Inspect the drive belts condition. Adjust / Replace as needed.
180 | Inspect the condition of the weather seals on both side columns.
190 | **********Electrically Operated Doors**********
200 | Check And Adjust Manual Disconnect.
210 | Check And Adjust Limit Switches.
220 | Check And Adjust Solenoid Brake.
230 | Check And Adjust Reversing Safety Switch.
240 | Check And Adjust Push Button Controls.
250 | Check, Clean And Adjust Electrical Controls.
260 | Check Shafts, Sprockets, Belts And Chains For Wear.
270 | Check Safety Edge and function of Photo Eye.
280 | Check Proper Operation for Treadle Switch Hose
290 | **********Fire Doors/Shutters**********
300 | Tested In Compliance With NFPA 80
310 | Check Fusible Link, Ensure Components Connected Properly.
320 | Perform Drop Test; Adjust As Required, Reset Door/Shutter.
330 | Findings Reported To Maintenance Supervisor

## ANCHOR-R-Q-01
ANCHOR-R-Q-01 | QUINQUENNIAL FALL PROTECTION ROOF ANCHORS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Qualified Vendor To Perform Load Test (Pull Test) On Fall Protection System
30 | Submit An Engineer-Stamped Letter Of Recertification & Report To Facility Operat
40 | Findings Reported To Maintenance Supervisor

## ANCHOR-R-A-01
ANCHOR-R-A-01 | ANNUAL ROOF ANCHORS INSPECTION
Sequence | Description
10 | Have anchors load tested
20 | Submit a safety report to Facility Operations
30 | Advise Facility Operations for any action required if deficiency is found

## AQ-S-01
AQ-S-01 | SEMI-ANNUAL INDOOR AIR QUALITY TEST
Sequence | Description
10 | Arrange with Hygienist from Environmental & Safety Management (ESM) for testing
20 | Location to be selected at random
30 | Review monitoring reports with FM Maintenance Supervisor

## BANCH-A-01
BANCH-A-01 | ANNUAL BUILDING ANCHORS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | All building anchor systems are to be inspected by a competent person
30 | To check for visual damage or disruptions found within the system
40 | Record is available on site for all workers to perform any work/visit in bldg
50 | Submit report as per requirements according to the CSA Z91 & OHS Codes - Part 9
60 | Review of the design drawings to ensure compliance with current regulation
70 | An assessment of the system to ensure compliance with engineered drawings
80 | Inspect all exposed, visible & accessible components for signs of distress
90 | Inspect of all adhesive and expansion fasteners
100 | Findings Reported To Maintenance Supervisor

## SAFETY-FPS-RA
SAFETY-FPS-RA-A | ANNUALLY RIGID ANCHOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Must be inspected by worker before it is used on each shift
30 | ***Permanent Anchor***
40 | Capable of safely withstand the impact force applied to it
50 | Has a min. breaking strength per attached worker of 16 kN or two times the max. arresting force
60 | Anchor is used in accordance with the manufacturer's specification
70 | Re-certified as specified by manufacturer if needed
80 | ***Temporary Anchor in Travel Restraint System***(If appicable)
90 | Has a min. breaking strength in any direction of at least 3.5 kN per worker attached
100 | Installed, used and remove as per manufacturer's specification
110 | Re-certified as specified by manufacturer if needed
120 | Permanently marked as being for travel restraint only
130 | Remove from use on the earliest od the date for work completion
140 | ***Temporary Anchor in Fall Arrest System***(If aplicable)
150 | Has a min. breaking strength per attached worker of 16 kN or two times the max. arresting force
160 | Installed, used and remove as per manufacturer's specification
170 | Re-certified as specified by manufacturer if needed
180 | ***Duty to use***
190 | Worker must ensure personal fall arrest system that is safely secured to an anchor
200 | Visually inspect the anchor prior to attaching a fall protection system
210 | Do not use a damages anchor after repaired, replaced or re-certified by professional engineer
220 | Findings Reported To Maintenance Supervisor

## ELD-A-01
REG-ELD-A | ANNUALLY ELEVATING DEVICE INSPECTION
Sequence | Description
10 | Perform safety inspections on elevating device as per Safety Codes Council Policy
20 | Report if deficiency is found and propose required actions if required

## ELEV-Q-01
ELEV-Q-01 | QUARTERLY ELEVATING & LIFT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per Elevating Device Code Regulation for inspection
30 | Refer to ASME A17.1-2007/CSA B44-07 (Sect 8.6) req and manufacturer standard
40 | Ensure all safety devices are functioning properly
50 | Ensure fire extinguisher is provided in elevator machine room
60 | ***For Electric Elevators***
70 | Keep lightly lubricate the suspension and compensating rope
80 | Keep clean for the governor wire ropes
90 | Lubricate the guide rails according to manufacturer's instruction
100 | Rails shall be kept clean and free of lint
110 | Check oil level of oil buffer
120 | Keep clean for the buffer plunger
130 | Safety mechanisms shall be kept lubricated and free of rust and dirt
140 | Maintain required clearance between safety jaws and rails
150 | Ensure proper operation of brakes
160 | Check Pit access door, keep close
170 | Cleaning of hoistway and pits
180 | Cleaning of top of cars
190 | Refastening of car-hoisting ropes on winding-drum machines (if applicable)
200 | Check the legible metal tag securely attached to wire rope fastening
210 | Check proper operation of governors
220 | Check all interlock devices of door system are operating properly
230 | Inspect the stopping accuracy at the landing
240 | Check overspeed and unintended car movement protection
245 | Test the Elevator Recall function for emergency
250 | ***For Hydraulic Elevators***
260 | Clean pressure tanks
270 | Check liquid level in pressure tanks
280 | Clean piston rods and hydraulic plungers
290 | Check oil level in oil ranks
300 | Examine the packing glands and seals
310 | Check any oil leakage. Correct as needed.
320 | Check flexible hoses and fittings
330 | Record of oil usage
340 | Check safety bulkhead
350 | To ensure seal is intact of relief-valve setting
360 | Check for any corrosion, correct as needed.
370 | Record activities and deficiencies in log books. Repair or replace immediately
380 | Findings reported to Property Manager

## ESC-Q-01
ESC-Q-01 | QUARTERLY ESCALTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per Elevating Device Code Regulation for inspection
30 | Refer to ASME A17.1-2007/CSA B44-07 (Sect 8.6) req and manufacturer's standard
40 | Ensure all safety devices are functioning properly
50 | Check the condition of handrails
60 | Check the clearance of step-to-skirt clearance
70 | Check the condition of combplates. Repair or replace as needed
80 | Check the condition of escalator steps
90 | Check the condition of skirt panel.
100 | Ensure required clearance of rollers, tracks and chains
110 | Check the function of antislide devices
120 | Check the condition of handrail guards
130 | Ensure proper operation of brakes
140 | Cleaning the escalators pit
150 | Ensure escalator landing plates are properly secured in place
160 | Check the function of motion detection devices if equipped
170 | Record activities and deficiencies in log books. Repair or replace immediately
180 | Findings reported to Property Manager

## ELD-B-01
ELD-B-01 | BIENNIAL ELEVATING DEVICE INSPECTION
1
Sequence | Description
10 | Perform safety inspections on elevating device as per Safety Codes Council Policy
20 | Report if deficiency is found and propose required actions if required

## HB-TE-01
HB-TE-01 | TRIENNIAL BOILER INSPECTION & CERTIFICATION (ABSA)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure Triennial Boiler Inspection has been performed prior to contacting ABSA
30 | Contact ABSA Inspector to inspect boiler
40 | Post inspection certificate in boiler room
50 | Findings Reported To Maintenance Supervisor

## PB-BA-01
PB-BA-01 | BIENNIAL POWER BOILER INSPECTION & CERTIFICATION (ABSA)
Sequence | Description | Type
10 | Ensure Annual Boiler Inspection has been performed prior to contacting ABSA | Checklist Item
20 | Contact ABSA Inspector to inspect boiler | Checklist Item
30 | Post inspection certificate in boiler room | Checklist Item

## LFT-SICC-Q
LFT-SICC-Q | QUARTERLY SCISSOR LIFT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to manufacturer's instruction requirement for maintenance
30 | Inpsect the electrical contactor
40 | Inspect the fuel tank check valve venting
50 | Inspect the tires, wheels and lug nut torque
60 | Confirm proper brake configuration
70 | Check the module tray latch components
80 | Visual inspect the hydraulic oil
90 | Inspect the hydraulic filter. Replace as needed.
100 | Inspect the battery balancer
110 | Inspect the electrical wiring
120 | Inspect the voltage inverter if equipped
130 | Check for open bulletins and owner registration
140 | Test the driver brake
150 | Test the drive speed - stowed position
160 | Test the drive speed - speed position
170 | Test the down limit switch, level sensor and pothole limit switches
180 | Test the platform gate proximity switches and the extension deck limit switch
190 | Check hydraulic arms for leaks
200 | Ensure machine is plugged into charging system
210 | Ensure OEM operators manual, and Inspection log is in weatherproof box
220 | Complete daily Inspection Sheet
Existing tasks in EAM (Monthly)
Sequence | Description
10 | Check battery water level
20 | Check oil reservoir
30 | Check hydraulic arms for leaks
40 | Check hoses for leaks
50 | Check tires for cuts & wear
60 | Check welds for stress
70 | Check wiring for condition & connection tightness
80 | Check control box for normal operation
90 | Ensure machine is plugged into charging system
100 | Ensure OEM operators manual, and Inspection log is in weatherproof box
110 | Complete daily Inspection Sheet

## LFT-SCIS-M-01
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to manufacturer's instruction requirement for maintenance
30 | Check for open bulletins and owner registration
40 | Inspect battery condition and battery balancer (refill water level if required)
50 | Inspect electrical wiring condition and electrical contactor
60 | Inspect voltage invertor (if equipped)
70 | Test the flashing beacons (if equipped)
80 | Inspect the hydraulic filter. Replace as needed.
90 | Check the module tray latch components
100 | Visual inspect the hydraulic oil
110 | Inspect the tires and wheels
120 | Confirm the proper brake operation
130 | Test the drive brake
140 | Test the drive speed - stowed position
150 | Test the drive speed - raised position
160 | Test the down limit switch, level sensor and pothole limit switches
170 | Test the platform gate proximity switches and the extension deck limit switch
180 | Check hydraulic arms for leaks
190 | Ensure machine is plugged into charging system
200 | Ensure OEM operators manual, and Inspection log is in weatherproof box
210 | Complete Inspection Sheet
220 | Recertification of scissor lift by contractor when required
230 | Findings Reported to Maintenance Supervisor

## LFT-SICS-A-01
LFT-SCIS-A-01 | ANNUAL SCISSOR LIFT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | This must be done by a qualified & trained vendor
30 | ***Functions and Controls***
40 | Machine has the latest control system software
50 | All joystick/toggle control return neutral / off position when released
60 | at ground and / or platform control stations.
70 | All functions and speed limits/cut-outs operate properly
80 | Manual descent system &/or auxiliary power system operates properly
90 | Load Sensing System operates properly
100 | Brakes operate properly
110 | Check all other machine controls, alarms, horn, display, indicators
120 | Ensure all above functions operate properly at platform & ground control station
130 | ***Platform Assembly***
140 | Platform installed and secure. Mounting hardware free of damage and secure
150 | Gate or chain installed and latches properly
160 | Platform guardrails and floor properly installed, secure and free of damage
170 | Extension deck properly installed and functions properly
180 | Locks at full extension and retraction
190 | Lanyard anchorage points secure, free of damage and labeled
200 | Fold-down rails installed properly. No loose or missing parts
210 | ***Scissor Arms***
220 | Scissor arms free of damage, cracks and distortion
230 | Safety props properly installed and function properly
240 | Inspect all nuts, bolts, shaft, shield, locking device & bearings
250 | Ensure for proper installation, secure, no excessive wear , cracks & distortion
260 | Cylinder pins, bearing & attach hardware secure, free of damage & excessive wear
270 | Arm pins, bearing & attach hardware secure, free of damage & excessive wear
280 | Arm pads and sliding blocks secure, free of damage & excessive wear
290 | ***Chassis***
300 | Wheel attached hardware torqued properly. No missing attach hardware
310 | Proper wheels/ tires installed. Inspect for excessive damage, wear & corrosion
320 | Check oscillating axle and lockout cylinders installed & secure (if app)
330 | Steering components are properly installed, secure and free of damage
340 | Check drive hubs for proper fluid level
350 | Leveling jacks or stabilizers operate properly (if app)
360 | Hydraulic trays and battery/engine compartment covers open and latch properly
370 | Pothole Protection System deploys and retracts properly
380 | Platform ladder properly installed, secure and free of damage
390 | Static strap is properly installed and secure
400 | ***Power System***
410 | Engine idle and throttle set at proper RPM (if app)
420 | Proper battery fluid level. Battery charger operates properly and accept charge
430 | Air and fuel filter properly services (if app)
440 | Proper coolant and engine oil level (if app)
450 | Proper fuel cap installed (if app)
460 | Exhaust system operate properly, secure and free of damage (if app)
470 | ***Hydraulic & Electrical System***
480 | All cylinders/actuators free of damage without evidence of leaks
490 | All areas around hydraulic components have no evidence of leaks
500 | Hydraulic oil system properly services and free of contaminants
510 | All hydraulic hoses, fittings & lines secure and free of damage and leaks
520 | All electrical connection tight, no corrosion or abrasions
530 | Pump and motor secure, free of damage and leaks
540 | All hydraulic pressure properly adjusted
550 | ***Manuals and Decals***
560 | Ensure Operation & Safety Manual and handbook in manual storage box
570 | All safety, capacity and instructional decals installed, secure and legible
580 | ***General***
590 | Machine is free of unauthorized modifications or additions
600 | Applicable Safety Bulletins completed
610 | Grease and lubricate per Service & maintenance manual
620 | Drive and operate machine to test all machine functions
630 | Complete Inspection Sheet by qualified vendor
640 | Recertification of scissor lift by qualified vendor when required
650 | Findings Reported to Maintenance Supervisor

## LFT-BOOM-A-01
LFT-BOOM-A-01 | ANNUAL BOOM LIFT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to manufacturer's instruction requirement for maintenance
30 | Below task plan is the minimum requirement to follow. The qualified & trained
40 | vendor is responsible to comply with all updated & applicable codes as required
50 | ####Drive Chassis####
60 | Inspect the Tires, Wheels and Lug Nut Torque
70 | Check the Oscillate Valve Linkage (if equipped)
80 | Confirm the Proper Brake Configuration
90 | Extendable Axle Wear Pads (if equipped)
100 | Check Drive Hub Oil Level and Fastener Torque
110 | ####Turntable Mechanicals and Hydraulics####
120 | Visual Inspection of the Hydraulic Oil
130 | Inspect the Hydraulic Filters
140 | Grease the Turntable Rotation Bearing
150 | Check Turntable Bearing Bolts
160 | Inspect for Turntable Bearing Wear
170 | ####Electrical####
180 | Inspect Electrical Contactors - Bi-energy models
190 | Inspect battery and electrical wiring
200 | ####Engine####
210 | Check the Exhaust System
220 | Check Generator Belts/Pulleys - Bi-energy models
230 | Check and Adjust the Engine RPM
240 | Perform Engine Maintenance (including parts replacement every 2 years)
250 | ####Functions and Controls####
260 | Check for Open Bulletins and Owner Registration
270 | Test the Ground Control Override
280 | Test the Alarm Package (if equipped)
290 | Test the Emergency Power System
300 | Test the Engine Idle Select Operation
310 | Test the Platform Self-leveling
320 | Test the Drive Brakes
330 | Test the Drive Speed - Stowed, Raised and Extended Position
340 | Test the Aircraft Protection System (if equipped)
350 | Test the Operator Protection Alarm (if equipped)
360 | Test the Bypass/Recovery Key Switch
370 | ####Boom(s) and Platform####
380 | Jib Rotate Bearing (if equipped)
390 | Grease the Platform Overload Mechanism
400 | Test Platform Overload
410 | Test Dual Capacity / Overload
420 | *****************************************************
430 | Ensure OEM operators manual, and Inspection log is in weatherproof box
440 | Recertification of boom lift by contractor when required
450 | Findings Reported to Maintenance Supervisor

## LFT-BOOM-Q-01
LFT-BOOM-Q-01 | QUARTERLY BOOM LIFT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to OHS Code and manufacturer's instruction requirements for maintenance
30 | Below task plan is the minimum requirement to follow. The qualified & trained
40 | vendor is responsible to comply with all updated & applicable codes as required
50 | ####Drive Chassis####
60 | Inspect the Tires, Wheels and Lug Nut Torque
70 | Check the Oscillate Valve Linkage (if equipped)
80 | Confirm the Proper Brake Configuration
90 | ####Turntable Mechanicals and Hydraulics####
100 | Visual Inspection of the Hydraulic Oil
110 | Inspect the Hydraulic Filters
120 | ####Electrical####
130 | Inspect Electrical Contactors - Bi-energy models
140 | Inspect battery and electrical wiring
150 | ####Engine####
160 | Check the Exhaust System
170 | Check Generator Belts/Pulleys - Bi-energy models
180 | Check and Adjust the Engine RPM
190 | ####Functions and Controls####
200 | Check for Open Bulletins and Owner Registration
210 | Test the Ground Control Override
220 | Test the Alarm Package (if equipped)
230 | Test the Emergency Power System
240 | Test the Engine Idle Select Operation
250 | Test the Platform Self-leveling
260 | Test the Drive Brakes
270 | Test the Drive Speed - Stowed, Raised and Extended Position
280 | Test the Aircraft Protection System (if equipped)
290 | Test the Operator Protection Alarm (if equipped)
300 | *****************************************************
310 | Ensure OEM operators manual, and Inspection log is in weatherproof box
320 | Recertification of boom lift by contractor when required
330 | Findings Reported to Maintenance Supervisor

## HB-A-02
HB-A-02 | ANNUAL BOILER INSPECTION & CERTIFICATION (ABSA)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure Annual Boiler Inspection has been performed prior to contacting ABSA
30 | Contact ABSA Inspector to inspect boiler
40 | Post inspection certificate in boiler room
50 | Findings Reported To Maintenance Supervisor

## HB-B-01
HB-A-02 | BIENNIAL BOILER INSPECTION & CERTIFICATION (ABSA)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure Biennial Boiler Inspection has been performed prior to contacting ABSA
30 | Contact ABSA Inspector to inspect boiler
40 | Post inspection certificate in boiler room
50 | Findings Reported To Maintenance Supervisor

## PV-QR-01
PV-QR-01 | QUADRENNIAL PRESSURE VESSEL INSPECTION & CERTIFICATION (ABSA)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure Quadrennial Inspection has been performed prior to contacting ABSA
30 | Contact ABSA Inspector to inspect the concerned pressure vessels
40 | Post inspection certificate in relevant plant room
50 | Findings Reported To Maintenance Supervisor

## PV-QQ-01
PV-QQ-01 | QUINQUENNIAL PRESSURE VESSEL INSPECTION & CERTIFICATION (ABSA)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Ensure Quinquennial Inspection has been performed prior to contacting ABSA
30 | Contact ABSA Inspector to inspect the concerned pressure vessels
40 | Post inspection certificate in relevant plant room
50 | Findings Reported To Maintenance Supervisor

## HB-A-01
HB-A-01 | ANNUAL HEATING BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per ASME BPVC Section VI (Chapter 8) requirement for inspection
30 | Perform Initial Visual Inspection Of Boiler And Clean Exterior.
40 | Remove Front Door And Top Cover Inspect All Boiler Components Note Anything Unus
50 | Inspect Heat Exchanger, Burner, Combust Chamber For Deterioration Or Corrosion.
60 | Inspect And Clean Thoroughly. While Disassembling, Check Gaskets And Replace.
70 | Inspect And Clean Combustion Blower Fan And Inlet Screen Of Any Dust Or Lint.
80 | Inspect Condensation Drain Line And Ensure In Working Condition
90 | Test Boiler Safety Relief Valve. Check That Relief Valve Seat Remains Closed
100 | Check If Relief Is Piped Directly To The Floor Drain
110 | If No Permanent Drip Tube, Install Within 50mm Of Nearest Floor Drain
120 | Inspect And Clean Combustion Blower Fan Net Screen Of Dust Or Lint
130 | Lubricate Motor, as required.
140 | Test The Low Water Cut Off Control For Proper Operation
150 | With Boiler Off, Drain Boiler To Low Water Cut Off, Boiler Should Not Come On
160 | Bypass Flow Switch Refill Boiler When Water Above Low Water Probe, Boiler Starts
170 | Turn Boiler Off Remove Flow Switch Bypass Turn Boiler On For Normal Operation.
180 | Check That Boiler Fires And Operates Properly.
190 | While Boiler Is Firing: Test The Flow Switch Operation.
200 | While Boiler Is Firing: Shut Off Circulating Pump The Gas Valve Should Close
210 | Reset And Return To Original Settings
220 | While Boiler Is Firing: Test The High Limit Control
230 | While Boiler Is Firing: Reduce Temp Until Switch Opens. Gas Valve Should Close
240 | Reset And Return To Original Settings
250 | Examine Flue Condensate Lines To Ensure There Is No Blockage
260 | Examine Flue Condensate Lines To Ensure Condensate Runs Freely To A Floor Drain
270 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow
280 | Fire Boiler. Follow Manufacturer's Instructions. Report Any Faults During Firing
290 | With Boiler Firing, Check Venting For Leakage Record Deterioration Or Corrosion
300 | Isolate Strainer On Each Heating Pump, Remove, Clean And Reassemble
310 | Use Portable Co Detector To Sniff Boilers And Associated Ductwork For Leaks
320 | Pre Pm Work CO Readings
330 | Post Pm Work CO Readings
340 | Inspect Intakes And Exhaust Flanges, Ductwork And Connections. Tighten As Req.
350 | Test flame detections devices
360 | Inspect Gas Piping for Proper Support and Tightness
370 | Blowing Down to Remove Sediments
380 | Slow Drain Test of Low-Water Cutoff
390 | Conduct routine maintenance of cir. pump and expansion tank (if applicable)
400 | Findings Reported To Maintenance Supervisor

## RE-BOILER-EL-M
RE-BOILER-EL-M | MONTHLY ELECTRODE STEAM BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to ASME Section VII, Section 301.3.6 - Guidelines for the care of power boilers for inspection
30 | Shut down boiler and turn off (lock out) power supply.
40 | Check all electrical connections for tightness.
50 | Check electrical contacts for discoloration, corrosion, or pitting.
60 | Check pressure relief (safety) valves for any weeping or leaks.
70 | Perform any other maintenance as recommended by the boiler manufacturer.
80 | Restart boiler in accordance with the Manufacturer’s instructions

## RE-BOILER-FT-A
CE-BOILER-FT-A | ANNUAL FIRETUBE BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to ASME Section VII, Section 300.5 - Guidelines for the care of power boilers for inspection
30 | (A) Combustion Chamber or Grate
40 | Check refractory and brickwork for burning, spalling, erosion, and deterioration; repair or replace as needed
50 | Check chamber and grate for bending and sagging of metal parts.
60 | Check for leaks around the seal between the combustion chamber and front and rear tubesheets.
70 | (B) Tubes — Gas Side
80 | Clean and inspect tubes on gas side; note the amount of soot deposit as a check on burner operation.
90 | Check initial tube passes for signs of overheating.
100 | Check tubes for signs of leakage.
110 | Check flanges and gaskets on front and rear heads and gas distribution partitions
120 | Check for signs of gasbypassing or leakage
130 | Clean out and inspect refractory in gas side of boiler heads
140 | Check for burnt and spalled refractory
150 | Check around staybolt and brace connections for signs of water leakage
160 | Check belled or rolled tube ends for cracks and signs of water leakage
170 | (C) Tubes and Shell — Water Side
180 | Check for scale and corrosion on tubes.
190 | Check for scale and corrosion on tubesheets.
200 | Check for scale and corrosion on staybolts and braces.
210 | Clean water side and take samples of excessive scaling for analysis and further treatment.
220 | Check for bent, sagging, or warped tubes or tubesheets due to overheating or hot spots
230 | Check pressure drop over gas passes
240 | Compare with previous readings at similar loads to determine cleanliness.
250 | Check for sagging or “bagging” of tubes above grate on horizontal-return tubular boilers.
260 | Check exit gas temperature; compare with steam temperature to determine the extent of fouling
270 | Check hot spots in refractory flame conditions and general conditions as visible through front and rear peeholes
280 | Check boiler drum for visible water leaks.
290 | Check the operation of safety features on combustion and water-level controls

## RE-BOILER-EL-A
RE-BOILER-EL-A | ANNUAL ELECTRODE STEAM BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to ASME Section VII, Section 301.3.6 - Guidelines for the care of power boilers for inspection
30 | Shut down boiler, drain water from system, and clean out all accumulated scale buildup, corrosion, and sludge
40 | Inspect electrodes for deterioration or erosion.
50 | If the boiler has jet-spray nozzles, check counter electrodes and nozzles.
60 | Remove any scale buildup.
70 | Check all pressure gages for accuracy.
80 | Remove and check circulation pump(s) and inspect for wear of the shaft bearings and pump impellers.
90 | Have safety valves inspected for wear and correct settings by an approved valve service agency.
100 | Inspect blowdown and blowoff valves for seat erosion and proper operation.
110 | Perform any other maintenance as recommended by the boiler manufacturer.

## RE-BOILER-EL-W
RE-BOILER-EL-W | WEEKLY ELECTRODE STEAM BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to ASME Section VII, Section 301.3.6 - Guidelines for the care of power boilers for inspection
30 | During operations, blow down the gage glass daily to ensure accurate level indication.
40 | If the boiler does not have an automatic blowdown, manually blow down daily to maintain proper boiler water conductivity
50 | Check and clean strainers in the water supply lines, cooling loops, feedwater pumps, and blowdown cooling lines
60 | Check levels in chemical feed system reservoirs.
70 | Check blowoff valves and lines for proper operation.
80 | Check for steam leaks at electrode insulators and circulation pump seals.
90 | Check to see if the desired pressure is being maintained in the system and the boiler.
100 | Perform any other maintenance as recommended by the boiler manufacturer.

## HB-M-01
HB-M-01 | MONTHLY HEATING BOILER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per ASME BPVC Section VI (Chapter 8) requirement for inspection
30 | Inspect Condensation Drain Line And Ensure In Working Condition.
40 | Test Boiler Relief Valve, Check That Relief Valve Seat Remains Closed After Test
50 | Check If Relief Is Piped Directly To The Floor Drain,
60 | If No Permanent Drip Tube, Install Within 50mm Of Nearest Floor Drain.
70 | Inspect And Clean Combustion Blower Fan inlet Screen Of Dust Or Lint.
80 | Lubricate Motor as required.
90 | Test The Low Water Cut Off Control For Proper Operation.
100 | With Boiler Off, Drain Boiler To Low Water Cut Off, Boiler Should Not Come On
110 | Test flame detections devices
120 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow
130 | Test limit controls.
140 | Test operating controls.
150 | Inspect fuel supply systems in boiler room area.
160 | Check condition of heating surfaces
170 | Perform combustion and draft tests
180 | Test low‐water fuel cutoff and /or water feeder
190 | Blowing down to remove any sediments if needed
200 | Maintenance Personnel to collect water sample from HVAC system
210 | Submit the sample to a contractor who provides water testing
220 | Findings Reported To Maintenance Supervisor

## EOC-DT-A-01
EOC-DT-A-01 | ANNUAL DIESEL FUEL TESTING ANALYSIS
Sequence | Description
10 | Collect and take fuel sample from main underground tank to a lab for analysis
20 | Refer to ASTM 975 Standard for testing
30 | Test density, distillation, flash point, cetane index, water and particulates
40 | Submission of analysis report from Lab
50 | Rectify the defects if so required

## RE-BOILER-FT-M
RE-BOILER-FT-M | MONTHLY FIRETUBE POWER BOILER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Inspect Condensation Drain Line And Ensure In Working Condition.
20 | Test Boiler Relief Valve, Check That Relief Valve Seat Remains Closed After Test
30 | Check If Relief Is Piped Directly To The Floor Drain,
40 | If No Permanent Drip Tube, Install Within 50mm Of Nearest Floor Drain.
50 | Inspect And Clean Combustion Blower Fan inlet Screen Of Dust Or Lint.
60 | Lubricate Motor as required.
70 | Test The Low Water Cut Off Control For Proper Operation.
80 | With Boiler Off, Drain Boiler To Low Water Cut Off, Boiler Should Not Come On
90 | Test flame detections devices
100 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow
110 | Test limit controls.
120 | Test operating controls.
130 | Inspect fuel supply systems in boiler room area.
140 | Check condition of heating surfaces
150 | Perform combustion and draft tests
160 | Test low‐water fuel cutoff
170 | Blowing down to remove any sediments if needed
180 | Findings Reported To Maintenance Supervisor

## RE-BOILER-FT-W
RE-BOILER-FT-W | WEEKLY FIRETUBE BOILER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Perform Initial Visual Inspection Of Boiler And Clean Exterior.
20 | Observe Operating Pressures, Temperatures and General Conditions.
30 | Determine Cause of Unusual Noises or Conditions, Make Necessary Corrections.
40 | Arrange For Repairs To Be Made At The First Indication of Defects, Leakage
40 | Check any Malfunction At Safety Relief Valves, Safety Devices or Operation Controls.
50 | Keep The Boiler Room Clean. Observe Precautionary Measures For Fire Safety.
60 | Ensure That There Is Adequate Combustion Air In The Boiler Room.
70 | Maintain Boiler Room Log & Record Various Routines And Tests That Are Peformed.
80 | Observe Condition Of Flame-Correct If Flame Is Smoky/Burner Starts With A Puff.
90 | Observe Operation Of Circulating Pump(s)
100 | Check That Boiler Fires And Operates Properly.
110 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow.
120 | Findings Reported To Maintenance Supervisor

## RE-BOILER-WT-M
RE-BOILER-WT-M | MONTHLY WATERTUBE POWER BOILER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Inspect Condensation Drain Line And Ensure In Working Condition.
20 | Test Boiler Relief Valve, Check That Relief Valve Seat Remains Closed After Test
30 | Check If Relief Is Piped Directly To The Floor Drain,
40 | If No Permanent Drip Tube, Install Within 50mm Of Nearest Floor Drain.
50 | Inspect And Clean Combustion Blower Fan inlet Screen Of Dust Or Lint.
60 | Lubricate Motor as required.
70 | Test The Low Water Cut Off Control For Proper Operation.
80 | With Boiler Off, Drain Boiler To Low Water Cut Off, Boiler Should Not Come On
90 | Test flame detections devices
100 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow
110 | Test limit controls.
120 | Test operating controls.
130 | Inspect fuel supply systems in boiler room area.
140 | Check condition of heating surfaces
150 | Perform combustion and draft tests
160 | Test low‐water fuel cutoff
170 | Blowing down to remove any sediments if needed
180 | Findings Reported To Maintenance Supervisor

## RE-BOILER-WT-A
CE-BOILER-WT-A | ANNUAL WATER TUBE POWER BOILER INSPECTION
Sequence | Description
1 | Pre Job Hazard Assessment Completed?
2 | Refer to ASME Section VII, Clause 106.4 - Guidelines for the care of power boilers for inspection
3 | For Watertube Boilers Inspection
4 | ***Drums, Headers, and Tubes — Water Side***
5 | Check steam drums(s) for corrosion, scale, pitting, or other metal reduction.
6 | Clean manhole seats, resurface if necessary, and replace gaskets.
7 | Check steam scrubber and dryer in steam drum (if applicable) for corrosion, deposits, erosion, security, and tightness of joints
8 | Check condition of all chemical feed and blowdown lines inside pressure parts for plugging, security, leaks, and orientation
9 | Check for freedom of expansion for drums and headers.
10 | Examine tubes for corrosion, excessive deposits, flare cracking, and pitting.
11 | Replace all handhole gaskets on headers. Examine handhole plates and stud threads.
12 | Make a complete water-side examination, and check for scale buildup as necessary.
13 | Measure scale thickness by using commercially available gage
14 | ***Drums, Headers, and Tubes — Fire Side***
15 | Check exterior of drums for signs of tube-roll leakage, corrosion, fly-ash erosion, or overheating.
16 | Measure and record the metal thickness at several selected locations.
17 | Repeat measurements at subsequent examinations and compare the values over time.
18 | Check condition of outside drum insulation and replace or repair as necessary.
19 | Examine drum and header supports for condition and check expansion clearance.
20 | Check all blowdown connections for expansion and flexibility of support. Examine all piping and valves for leaks.
21 | Visually check water wall tubes and fins (if applicable) for cracks.
22 | Check exterior of all tubes for corrosion, buildup, erosion, blisters, and sagging.
23 | Examine tubes at soot blower for signs of steam impingement.
24 | Examine exterior of headers for corrosion, erosion, thermal cracking, and condition of insulation.
25 | *** Superheater***
26 | Examine superheater header and tubes for corrosion, erosion, and overheating.
27 | Measure and record the metal thickness at several selected locations.
28 | Repeat measurements at subsequent examinations and compare the values over time.
29 | Check for erosion on tubes due to impingement at soot blower location.
30 | Check superheater header and tubes for complete freedom of expansion.
31 | Check for cleanliness and security of superheater vent and drain.
32 | Examine superheater header and tube supports for security.
33 | ***Economizer***
34 | Check interior of tubes and headers where possible for corrosion, oxygen pitting, and scale.
35 | Check exterior of tubes and headers for corrosion, erosion, and deposits.
36 | Check particularly at soot blower locations for erosion on tubes due to impingement and leakage.
37 | Check for cleanliness and security of vent and drain connections and valves.
38 | Check exterior of economizer casing for leaks and tightness of access doors.
39 | Check condition of casing insulation.
40 | Overhaul all water valves. Check for leaks.
41 | Check condition of supporting steel.
42 | ***Refractory, Casing, and Baffles***
43 | Check furnace tile, brick, and castable refractory for loose, spalled, or missing pieces.
44 | Examine soot and ash hoppers for eroded refractory and condition of seals.
45 | Check for deterioration of burner tile and signs of flame impingement.
46 | Inspect condition of supporting steelwork where visible.
47 | Check exterior of furnace casing for bent, broken, or bowed sheets. Patch or repair as necessary.
48 | Check all access doors, lancing doors, etc., for tightness. Renew gaskets as required.
49 | Test furnace for air leaks, seal up all leaks
50 | Check condition of all baffle tile and caulking with particular attention to signs of leakage and security of supports
51 | ***Water Columns***
52 | Check gage glasses for leaks, cleanliness, and visibility.
53 | Check illuminators, reflectors, and mirrors for cleanliness and breakage.
54 | Check operation and condition of gage cocks and valves.
55 | Examine chains and pulleys, if used. Repair or replace as necessary.
56 | Ensure that water column is free to expand with boiler.
57 | Check water column piping to drums for leaks, internal deposits, and missing insulation.
58 | Check condition of high- and low-water alarms and trips
59 | ***Feedwater Regulator***
60 | Examine valve externally for leaks, operability, and cleanliness.
61 | Check connecting lines and mechanisms for proper function.
62 | If overhaul is necessary, consult manufacturer’s instructions before proceeding
63 | ***Soot Blowers***
64 | Check alignment of all soot blower hangers, and check tightness of hanger bolts.
65 | Check soot blower elements for distortion, worn hanger bearings, tube rubbing,
66 | Check condition of element nozzles, element breakage or cracking
67 | Ensure freedom of movement, effective lubrication, correct adjustment, and travel.
68 | Check condition of wall boxes. They should be sealed and secure.
69 | Check condition of moving parts, valves, and packing in soot blower head. Replace packing.
70 | Check position of elements for signs of steam impingement on tubes.
71 | Check each soot blower for correct blowing arc and direction of rotation.
72 | Pack the swivel tube gland and check swivel tubes for erosion and corrosion.
73 | Check gooseneck fittings for erosion and corrosion.
74 | Check supply piping and valves for leaks.
75 | Check condition of drain piping and valves. Ensure that supply piping slopes away from soot blower head.
76 | ***Valves***
77 | Check condition and operation of all feedwater, blowdown, drain, and other valves
78 | Replace parts as necessary and repack
79 | ***Safety Valves***
80 | Check discharge and drain piping for security, condition, and allowance for boiler expansion
81 | Test operation of valves by steam pressure and adjust them to open and close at the proper pressure
82 | Check condition of valve nozzle and disk seats. Lap seats, if required, in accordance with Manufacturer’s instruction
83 | Record set pressures and blowdown in the boiler log.
84 | Check condition of valve nozzle and disk seats. Lap seats, if required, in accordance with Manufacturer’s instruction
85 | Check condition of valve internal parts for corrosion, galling, and wear. Recondition or replace as needed
86 | Check condition of valve springs for pitting, cracking, resiliency, and end coil squareness
87 | Check spindle for straightness and adjusting ring threads for freedom of movement.
88 | ***Windbox***
89 | Check air dampers and vanes in windbox for corrosion and erosion.
90 | Check damper and vane operating mechanism.
91 | Check windbox insulation and repair as necessary.
92 | Check condition and operation of all of windbox access doors, peepholes, and cover plates. Check for air leaks.
93 | Check flame scanners for unobstructed view of the flame.
94 | Check ignitor equipment for condition of spark assembly, wiring, and wiring insulation.
95 | ***Gas Firing***
96 | Check condition of gas nozzles for erosion, burning, or plugging.
97 | Check operation of air-control damper mechanism.
98 | Check setting and operation of pressure-regulating valve.
99 | Check all piping and valves for leaks.
100 | Check safety shutoff valves for leakage; repair as necessary.
101 | ***Oil Firing***
102 | a) Fuel Oil Pumps
103 | Check for excessive clearances in driver
104 | Check for excessive backlash in driver
105 | Check for worn bearings in driver
106 | Check for leakage
107 | Check for wear in steam cylinder and piston
108 | Check for wear in oil cylinder and piston
109 | Check condition of oil and steam cylinder piston rings
110 | Check setting, operating, and wear of steam valves
111 | Check condition and seating of oil valves
112 | Check leaks from stuffing boxes and scoring of piston rods
113 | Check condition of steam strainers
114 | (b) Fuel Oil Heaters
115 | Remove tube bundle and clean off deposits on oil side.
116 | Examine steam side and oil side for corrosion and erosion.
117 | Check freedom of vents and drains.
118 | Check condition of insulation and repair as necessary.
119 | Check for tubesheet and tube leaks.
120 | Check condition, operation, and setting of relief valves.
121 | (c) Burners, Valves, and Piping
122 | Check setting and operation of pump-discharge pressure regulators.
123 | Check setting and operation of pressure relief valves on pump discharge.
124 | Check condition and operation of steam-pressure-reducing valve on oil heater.
125 | Clean and check oil suction strainer.
126 | Check and calibrate pressure gages and thermometers.
127 | Clean and check steam strainer.
128 | Check operation of oil heater condensate steam trap.
129 | Recondition all shutoff and adjusting valves as necessary.
130 | Perform leak check on safety shutoff valves after reconditioning.
131 | Clean and examine oil burners.
132 | Check for leaks at all connections.
133 | ***Air Heater***
134 | (a) Tubular or Plate Type
135 | Check gas side for plugging and buildup at inlet, and for corrosion and erosion at outlet.
136 | Check air side for corrosion and leaks.
137 | Remove all gas-side deposits. If washed, use an alkali rinse; if firing, use sulfur-bearing fuels.
138 | (b) Regenerative or Ljungstrom Type
139 | Check cold end section of heater surface for wear, plugging, and corrosion.
140 | Check condition of radial and circumferential seals on both hot and cold ends.
141 | Check condition of gear drive.
142 | Check operation and condition of soot blower (if fitted).
143 | Check effectiveness of bearing cooling.
144 | ***Fans***
145 | (a) Forced Draft and Primary Air Fans
146 | Check fan housing and rotor for corrosion, erosion, and signs of housing leaks.
147 | Check rotor for loose rivets or welds.
148 | Check clearance between rotor and fan housing.
149 | Check condition and operation of inlet vane operating mechanism.
150 | Check bearings for wear, clearance, lubrication, and cooling.
151 | Check coupling alignment at operating temperature.
152 | (b) Induced Draft Fans
153 | Check fan housing and housing liners for erosion, corrosion, fly-ash deposit, and housing leakage.
154 | Check fan rotor and liners for erosion, corrosion, fly-ash deposit, and weakening of rivets and welds.
155 | Check clearance between rotor and fan housing.
156 | Check condition of shaft seals.
157 | Check condition of inlet vanes and operating mechanism.
158 | Check bearings for wear, clearance, lubrication, and cooling.
159 | Check coupling alignment at operating temperatur
160 | ***Dampers***
161 | Check that linkage arms are secure on the blade shafts.
162 | Check to see that the blade(s) follow through the open to closed position as indicated on the linkage arm sector plate
163 | Check for indications of inservice binding, and ensure that clearances are adequate for expansion.
164 | Check to see that minimum stops, where required, are in place.
165 | Check that wear and deterioration on the sealing strips on tight closure dampers
166 | Check that damper blades are commercially clean, and the metal is not corroded or eroded.
167 | Check bearings for adequate lubrication
168 | Check for wear of internal bearings or link joints.
169 | Check flues and ducts for debris.
170 | With remote-controlled dampers, check to see that the drive strokes through the full range without binding.
171 | Check for safeguard permissive and interlock circuitry are operating properly
172 | Conduct Operating Checks
173 | ***Leakage***
174 | Check for any flue gas, steam, or water leaks.
175 | Check for steam leaks at superheater headers and tube joints.
176 | Check for air leaks around doors, seals, and furnace.
177 | ***Refractory***
178 | Check condition of burner throat refractory.
179 | Check for slag buildup on refractory.
180 | Check for missing insulation on headers and drum.
181 | ***Burners***
182 | Check for burner wear by noting flame shape and completeness of combustion.
183 | Check ease of operation of burner vanes. This will indicate burner mechanism condition.
184 | ***Superheater Tubes***
185 | Check for a change in pressure drop through the superheater, indicating internal condition of the tubes
186 | ***Drums***
187 | Check the steam quality. This will indicate the condition of steam scrubbers and separators.
188 | Check for noises in drums. This may be caused by loose connections of drum internal piping.
189 | ***Soot Blowers***
190 | Check steam pressure to soot blowers and blowing pressure.
191 | Check steam pressure at soot blower inlet, breakage of the element or missing nozzles for decrease in pressure
192 | Check pressure in supply piping with main supply valved out.
193 | ***Economizer and Air Preheater***
194 | Check for a variation in temperature differences over both units at constant load, indicating deposits or bypassing
195 | ***Pressure Variations***
196 | Check for an increase in pressure drop over any part of the system at constant load, indicating deposits or buildup.
197 | Check for a decrease in pressure drop over any part of the system at constant load, indicating a misplaced or bypassed baffle
198 | ***Furnace and Casing***
199 | Check the extent of expansion and contraction of pressure parts during start-up and shutdown.
200 | Check header support hangers are always in tension. Tighten as needed

## HB-W-01
HB-W-01 | WEEKLY HEATING BOILER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Observe operation of circulating pumps (if applicable)
20 | As per ASME BPVC Section VI (Chapter 8) requirement for inspection
30 | Perform Initial Visual Inspection Of Boiler And Clean Exterior.
40 | Observe Operating Pressures, Temperatures and General Conditions.
50 | Determine Cause of Unusual Noises or Conditions, Make Necessary Corrections.
60 | Arrange For Repairs To Be Made At The First Indication of Defects, Leakage
70 | Check any Malfunction At Safety Relief Valves, Safety Devices or Operation Contr
80 | Keep The Boiler Room Clean. Observe Precautionary Measures For Fire Safety.
90 | Ensure That There Is Adequate Combustion Air In The Boiler Room.
100 | Maintain Boiler Room Log & Record Various Routines And Tests That Are Performed.
110 | Observe Condition Of Flame-Correct If Flame Is Smoky/Burner Starts With A Puff.
120 | Observe Operation Of Circulating Pump(s)
130 | Check That Boiler Fires And Operates Properly.
140 | Check Fuel Supply, Pilot And Main Flame And Record Applicable Colour Blue/Yellow
150 | Findings Reported To Maintenance Supervisor

## RE-BOILER-WT-W
RE-BOILER-WT-W | WEEKLY WATERTUBE BOILER INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Perform Initial Visual Inspection Of Boiler And Clean Exterior.
20 | Observe Operating Pressures, Temperatures and General Conditions.
30 | Determine Cause of Unusual Noises or Conditions, Make Necessary Corrections.
40 | Arrange For Repairs To Be Made At The First Indication of Defects, Leakage
40 | Check any Malfunction At Safety Relief Valves, Safety Devices or Operation Controls.
50 | Keep The Boiler Room Clean. Observe Precautionary Measures For Fire Safety.
60 | Ensure That There Is Adequate Combustion Air In The Boiler Room.
70 | Maintain Boiler Room Log & Record Various Routines And Tests That Are Peformed.
80 | Observe Condition Of Flame-Correct If Flame Is Smoky/Burner Starts With A Puff.
90 | Observe Operation Of Circulating Pump(s)
100 | Check That Boiler Fires And Operates Properly.
110 | Check Pilot And Main Flame And Record The Applicable Colour Blue/Yellow.
120 | Findings Reported To Maintenance Supervisor

## RTU-S-01-R21
RTU-S-01-R21 | SEMI-ANNUAL ROOF TOP UNIT INSPECTION (RFP)
Sequence | Description
10 | **COMMON TASKS**
20 | Complete Pre Job Hazard Assessment
30 | Perform pre-work CO and gas safety check
40 | Vacuum Unit (Including Blower and Burner Compartment)
50 | Check Unit Access Panels’ Fastening and Access Panel Gasket for Damage.
60 | Replace Belt
70 | Ensure blower wheel rotates freely
80 | Lubricate As Per Manufacturer’s Recommendations
90 | Perform electronic combustion analysis and make adjustments as needed
100 | Verify Motor Amperage is within nameplate range
110 | Inspect and clean condensate pans and drains
120 | Verify unit safety controls are functioning
130 | Inspect all filters including MERV 13, replace or clean as needed
140 | Perform post-work CO and gas safety check
150 | Findings Reported To City Representative
160 | **FALL HEATING INSPECTION**
170 | Clean Burner Chamber
180 | Inspect Combustion Intake And Venting For Leakage, Blockage And Damage
190 | Visually Inspect Heat Exchanger
200 | Check dampers as required
210 | Check neutralizing agents and condition of condensate drain lines (if app)
220 | Inspect and clean desiccant wheel and associated belts/chains and motor
230 | **SPRING COOLING INSPECTION**
240 | Check refrigerant charge and perform leak check
250 | Inspect and Clean condenser and evaporator coil
260 | Comb all damaged fins
270 | Check Compressor Oil Level and evidence of oil leaks (if applicable)
280 | Check Refrigerant Operating Temperature And Pressures (if applicable)
290 | Check Condenser Fans And Tighten Set Screws (if applicable)
300 | Verify motor amperages are within nameplate ranges
310 | Findings Reported To City Representative

## PD-SMP-CO-A
PD-SMP-A | ANNUAL SETPIC TANK CLEAN OUT
Sequence | Description
10 | Job Hazard Assessment Completed?
20 | Position the drain cleaning machine with associated accessories
30 | Select the proper length and size of vacuum hose
40 | Place pylons or barriers around the immediate work space.
50 | Engage the blower and begin to remove the waste from septic tank
60 | Checking the fluid levels in the septic tank
70 | Once the septic tank has been cleaned, remove the cleaning machine at once
80 | Cover the tank
90 | Make sure the waste has cleared the vacuum hose
100 | Shut down the blower, break apart the hoses and strap them down for travel
110 | Ensure that the work area is clear of all tools
120 | Fill out the proper disposal manifest
130 | Transport the waste to the City of Calgary Waste Disposal Site

## ANCHOR-R-A-02
ANCHOR-R-A-02 | ANNUAL FALL PROTECTION ROOF ANCHORS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Qualified Vendor Required To Inspect & Certify Fall Protection System
30 | Visually Inspect All Exposed & Accessible Components
40 | Perform Minor System Maintenance If Required
50 | As per “OHSafety Code – Alberta Reg. 2019 – Part 9 Fall Protection, Sect. 152”
60 | Anchor should be capable of safely withstand the impact force applied to it
70 | Has a min. breaking strength per attached worker of 16 kN
80 | or two times the max. arresting force
90 | Re-certified as specified by manufacturer if needed
100 | Submit An Engineer-Stamped Letter Of Recertification & Report To Facility Operation
110 | Findings Reported To Maintenance Supervisor

## SAFETY-W-A-01
SAFETY-W-A-01 | ANNUAL WORKPLACE SAFETY INSPECTION (Mechanical and Electrical Room)
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Conduct a safety inspection of the Shop Area, Mechanical and Electrical rooms
20 | Fill-out and submit a Workplace Inspection - Operations form X-516
30 | Findings reported to Maintenance Supervisor

## RTU-A-01
RTU-A-01 | ANNUAL ROOFTOP UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Electrical & Fastening Devices Are Secure. Adjust, Tighten As Required.
30 | Vacuum Unit Internals Thoroughly. (Including Blower And Burner Compartment)
40 | Replace Belt
50 | Turn Blower Wheel(S) By Hand To Check Blower Alignment & Bearing Operation.
60 | Remove Flame Rod, Clean And Inspect.
70 | Lubricate Motor And Fan Bearings As Per Manufacturer’S Recommendations.
80 | Inspect And Clean Desiccant Wheel. (Dehumidifiers Only).
90 | Test Dampers & Linkage Hardware. Operate Dampers Full Range From Open To Close
100 | Test Unit Firing, Mfr Operational Checklists. Observe Through The Access Door
110 | Test Crankcase Heater Operation
120 | Check And Record Refrigerant Discharge/Suction Pressures Discharge Pressure (if gauge present)
130 | Check And Record Refrigerant Discharge/Suction Pressures Suction Pressure (if gauge present)
140 | Perform Electronic Refrigerant Leak Check. Record Observations.
150 | Inspect Condenser Fins/Evaporator Coil For Damage; Comb As Required
160 | Note Any Unusual Vibrations Which May Require Vibration Analysis.
170 | Clean return air filters. Replace if needed
180 | Clean and repaint any corroded surface
190 | Clean the refrigerant coils
200 | Check the drain pan and condensate piping to avoid blockage
210 | Manual rotate condenser fan to ensure free movement
220 | Clean burner area, verify gas heat system operates properly
230 | Visually inspect exposed ductwork and piping insulation. Correct as needed
240 | Check compressor oil levels and any leaks. Repair or adjust as needed
250 | The Safety Shut Off Valves must be tested on at least an annual basis or as per the manufacturer’s recommendations which ever is less
260 | Regulators with vent terminals must have yearly cleaning of the screen.
270 | The burner be inspected once each year.
280 | Remove any scale that may have accumulated on the burner plates.
290 | Ensure that the holes on the burner plates and gas orifices are completely clear of foreign material.
300 | Findings Reported to Maintenance Supervisor
Existing tasks in EAM
Sequence | Description
10 | Check Electrical & Fastening Devices Are Secure. Adjust, Tighten As Required.
20 | Vacuum Unit Internals Thoroughly. (Including Blower And Burner Compartment)
30 | Replace Belt
40 | Turn Blower Wheel(S) By Hand To Check Blower Alignment & Bearing Operation.
50 | Remove Flame Rod, Clean And Inspect.
60 | Lubricate Motor And Fan Bearings As Per Manufacturer’S Recommendations.
70 | Measure And Record Motor Amperages - Low Speed Supply Fan Motor Volts
80 | Measure And Record Motor Amperages - Low Speed Supply Fan Motor Amps
90 | Measure And Record Motor Amperages - High Speed Supply Fan Motor Volts
100 | Measure And Record Motor Amperages - High Speed Supply Fan Motor Amps
110 | Measure And Record Motor Amperages - Low Speed Return Fan Motor Volts
120 | Measure And Record Motor Amperages - Low Speed Return Fan Motor Amps
130 | Measure And Record Motor Amperages - High Speed Return Fan Motor Volts
140 | Measure And Record Motor Amperages - High Speed Return Fan Motor Amps
150 | Measure And Record Motor Amperages - Dessicant Wheel Motor Volts
160 | Measure And Record Motor Amperages - Dessicant Wheel Motor Amps
170 | Measure And Record Motor Amperages - Compressor Motor Volts
180 | Measure And Record Motor Amperages - Compressor Motor Amps
190 | Measure And Record Motor Amperages - Condenser Fan Motor Volts
200 | Measure And Record Motor Amperages - Condenser Fan Motor Amps
210 | Inspect And Clean Desiccant Wheel. (Dehumidifiers Only).
220 | Test Dampers & Linkage Hardware. Operate Dampers Full Range From Open To Close
230 | Test Unit Firing, Mfr Operational Checklists. Observe Through The Access Door
240 | Inspect And Clean Contactors. Replace If Required
250 | Inspect Fuses. Replace Damaged Or Broken Fuses.
260 | Test Crankcase Heater Operation
270 | Check And Record Refrigerant Discharge/Suction Pressures Discharge Pressure
280 | Check And Record Refrigerant Discharge/Suction Pressures Suction Pressure
290 | Perform Electronic Refrigerant Leak Check. Record Observations.
300 | Inspect Condenser Fins/Evaporator Coil For Damage; Comb As Required
310 | Note Any Unusual Vibrations Which May Require Vibration Analysis.
320 | Check Unit Component Fastening Devices To Ensure All Are Secure.
330 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
340 | Pre Job Hazard Assessment Completed?

## SAFETY-FPS-ESL
SAFETY-FPS-ESL-A | ANNUALLY ENERGY (SHOCK) ABORBER & LANYARD INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Must be inspected by worker before it is used on each shift
30 | Keep free from substance and condition to avoid deterioration of equipment
40 | Re-certified as specified by manufacturer if needed
50 | Approved by CSA Standard Z259.11-05, Energy absorbers and lanyards
60 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for personal fall arrest systems, subsystems and components
70 | Equip with shock absorber for full body harness and a lanyard
80 | Class E4: Standard 4.0 kN energy absorber or lanyard intended for general use in fall arrest systems. For workers from 100 lb to 254 lb
90 | Class E6: Heavyweight 6.0 kN energy absorber or lanyard intended for use in fall arrest systems for workers from 200 lb to 386 lb
100 | Lanyard used by a worker is made of wire rope or other material appropriate to the hazard
110 | Do not store around chemicals and wet place
120 | Selecting the shortest length lanyard that without interfering work performance of duties
130 | Securing the lanyard to an anchor no lower than the worker’s shoulder height
140 | Findings Reported To Maintenance Supervisor

## BP-01
BP-01 | ANNUALLY BACKFLOW PREVENTOR DEVICE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to City of Calgary - Bylaw Water Utlility 40M2006 requirement for inspection
30 | Inspect and test the function of Double Check Valve Assmeblies (DCVA)
40 | Inspect and test the function of Reduced Pressure Principle Assemblies (RP)
50 | Inspect and test the function of Pressure Vaccum Breaker Assemblies (PVB/SRPVB)
60 | Inspect and test air gaps
70 | If the device fails the initial test, retest is required
80 | Submission of Form E1059 to Water Services
90 | Findings Reported To Maintenance Supervisor

## SAFETY-FPS-FBH
SAFETY-FPS-FBH | ANNUALLY FULL BODY HARNESS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Approved by CSA Standard CAN/CSA Z259.10-06, Full Body Harnesses
30 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for personal fall arrest systems, subsystems and components
40 | Keep free from substance and condition to avoid deterioration of equipment
50 | Re-certified as specified by manufacturer if needed
60 | The harness must be worn, used and maintained as per manufacturer's instruction
70 | Worker using a personal fall arrest system must wear full body harness
80 | Findings Reported To Maintenance Supervisor

## GAS-A-01
LS-CO-DET-A | ANNUAL GAS (CO, NO2 & FREON) DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 72 - Chapter 14 (14.3.1 & 14.4.3.1) requirement for inspection
30 | Inspect and clean detectors
40 | Calibrate Detectors by using calibration kit as per manufacturer's instruction
50 | Set the sensor to zero on the display screen
60 | Connect the regulator to calibration gas cylinder
70 | Adjust the flow rate to the indicated rate
80 | Connect tubing from regulator to sensor calibration cap
90 | Let the gas flow at least 3 mins before starting calibration
100 | Confirm success message displays on unit screen after calibration
110 | Carry out bump and functional test as per manufacturer's instruction
120 | Press the test buttons for sound and flashing LED operation (if applicable)
130 | Verify location on floor plan and condition
140 | Verify operation of audible and visual alarms and signal
150 | Inspect lithium batteries and tightness of connection (if applicable)
160 | Check the expiry date of unit and replace as per manufacturer's recommendation
170 | Check ULC marking for any new detectors
180 | Check interlock function (exhaust fan) once activate the alarm (if applicable)
190 | Review and rectify any defects in inspection report by contractor
200 | Findings Reported To Maintenance Supervisor
Existing task in EAM (SD-01) - COC Annual Smoke Detector Inspection
Sequence | Description
10 | Check The Keys Within The Lock Boxes To Ensure That They Are Correct
20 | Make Sure Keys Will Allow Emergency Responders Access Into The Facility
30 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
40 | Pre Job Hazard Assessment Completed?
Existing task in EAM (PK-CO-01) - PK CO Detector Calibration
Sequence | Description
10 | Inspect and clean sensor
20 | Inspect BAS sensor reading against the following:
30 | An alternate calibrated sensor device readout (ISO 9000 standard traceable) OR
40 | A buffer solution or gas at calibrated concentrations
50 | Inspect, test, adjust and record observations. Allowable error: +/- 0.05ppm (CO)
60 | Before Calibration: Actual Reading:
70 | Before Calibration: BAS Reading:
80 | Intercept Adjust (record value):
90 | Post Calibration - Actual Reading:
100 | Post Calibration - BAS Reading:
110 | BAS sensor replacement required?
Existing task in EAM (GAS-01) - COC Annual Gas Detector Inspection
Sequence | Description
10 | Inspect CO, NO2 & Freon Detectors.
20 | Calibrate Detectors
30 | Clean Detectors
40 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
50 | Pre Job Hazard Assessment Completed?
Existing task in EAM (RC-DA-01) - RC Annual Ammonia Detectors Inspection
Sequence | Description
10 | NOTIFY ALARM MONITORING COMPANY TO PLACE SYSTEM ON TEST
20 | Generate virtual 100ppm & 300ppm alarm signals to test program sequence of
30 | operation of detection system:
40 | 1st Stage (100 ppm) and 2nd Stage (300 ppm) ammonia alarms
50 | Generate Stage 1 alarm, 100 ppm or greater ammonia concentration, the first
60 | stage of the alarm system is activated and a horn begins to sound in the office
70 | area. Ventilation unit and exhaust fan are energized. Dialer sends alarm signal
80 | to monitoring company.
90 | Generate Stage 2 alarm, 300 ppm or greater ammonia concentration, the second
100 | stage of the alarm system is activated and a horn begins to sound in the office
110 | area. A blue strobe light is activated outside the compressor room. Ventilation
120 | unit and exhaust fan are energized at high level. Equipment runs until ammonia
130 | level has dropped below 50 ppm for 120 seconds. Dialer sends alarm signal to
140 | monitoring company.
150 | Record observations as follows: Ammonia Virtual Alarm Test
160 | 100 ppm - Office Horn activated
170 | 100 ppm - Exhaust Fan energized
180 | 100 ppm - Make-up Air Unit energized
190 | 100 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
200 | 300 ppm - Office Horn activated
210 | 300 ppm - Blue Strobe activated
220 | 300 ppm - Exhaust Fan energized
230 | 300 ppm - Make-up Air Unit energized
240 | 300 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
250 | Inspect, verify and record operation of switching indicated below:
260 | REFRIGERATION ROOM VESTIBULE SWITCHING
270 | Occupied Switch ON/OFF Energizes/de-energizes exhaust fan and make-up ai unit.
280 | Emergency Ventilation Switch Energizes (START ONLY) exhaust fan and make-up
290 | air unit at maximum volume, as well as blue strobe light and office horn. Alarm
300 | signal sent to monitoring company.
310 | REFRIGERATION ROOM SWITCHING (AT ROOM EXITS)
320 | Emergency Ventilation Switch - START / STOP
330 | Vestibule Occupied switch Passed?
340 | Vestibule Emergency ventilation switch Passed?
350 | Refrigeration Room manual switch exit 1 Passed?
360 | Refrigeration Room manual switch exit 2 Passed?
370 | Verify all alarm signals received by monitoring company Passed?
380 | Verify BAS display in agreement with tests Passed?
390 | 1. Replace ammonia element in NH3 sensor
400 | 2. Perform a 300 ppm gas test on the NH3 sensor and calibrate as below (Passed?)
410 | SENSOR CALIBRATION. Record observation below - Allowable error: +/- 5% ppm (NH3)
420 | BEFORE CALIBRATION - Actual Reading
430 | BEFORE CALIBRATION - BAS Reading
440 | POST CALIBRATION - Actual Reading
450 | POST CALIBRATION - BAS Reading
460 | 3. Verify LCD display read out for ammonia sensor located on the vestibule Panel
470 | Record observation below - Allowable error: +/- 5% ppm (NH3)
480 | LCD Panel Reading:
490 | NOTIFY ALARM MONITORING COMPANY TO TAKE SYSTEM OFF TEST

## GAS-S-01
GAS-S-01 | SEMI-ANNUALLY GAS DETECTOR (CO, NO2 & FREON) DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 72 - Chapter 14 (14.3.1) & NFPA 720 - Chapter 8 (8.3.1) requirement for inspection
30 | Carry out visual inspection to detectors
40 | Carry out bump and functional test as per manufacturer's instruction
50 | Inspect and clean detectors
60 | Verify the detectors are mounted properly
70 | Verify location and condition
80 | Findings Reported To Maintenance Supervisor

## Elect PM Interval (Code)
CLASS / TYPE | SYSTEM HIERARCHY | EQUIPMENT DESCRIPTION | Thermal Scanning in RFP | Recommendation from PM Team - Interval (Months)
ELECTRICAL
EL-EQUIP-HV (Over 750V)
|  | Power Distribution Switchgear and panel boards | √ | 12
|  | Power Transformer (Liquid Filled) | √ | 12
|  | Power Transformer (Dry-type) | √ | 12
|  | Power Cables | √ | 6
|  | High voltage power circuit breaker | √ | 12
EL-EQUIP-LV (30V - 750V)
|  | Power Distribution Switchgear and panel boards | √ | 12
|  | Power Transformer (Liquid Filled) | √ | 12
|  | Power Transformer (Dry-type) | √ | 12
|  | Power Cables | √ | 6
|  | Metal-enclosed busways | √ | 12
|  | Disconnect Switch & Circuit Switcher | √ | 12
|  | Circuit Breaker (Insulated & Moulded case) | √ | 12
|  | Low voltage power circuit breaker | √ | 12
|  | Protection, Control and Metering devices | √ | 12
|  | Instrument Transformer - CTs | √ | 12
|  | Instrument Transformer - VTs | √ | 12
|  | Motors (Rotating Machine & Pumps) | √ | 3
|  | Motor Control Centers (MCC) | √ | 12
|  | Variable Frequency Drive | √ | 36
|  | Medium voltage motor starters | √ | 12
|  | Surge Arrestor | √ | 12
|  | Capacitors (Power Factor Correction), e.g. WHMSC, EOC & MUMUN | √ | 3
|  | Reactors (Power Factor Correction) | √ | 3
|  | Uninterruptable Power Supply | √ | 12
|  | SCADA (For Future CCOM Onboarding) | √ | 12
|  | Emergency Generator | √ | 6
|  | Automatic Transfer Switch | √ | 12
EL-SYS
|  | Grounding Fault Protection Systems | √ | 12

## Elect PM Interval
CLASS / TYPE | SYSTEM HIERARCHY | EQUIPMENT DESCRIPTION | [9 empty] | Frequency | Task Plan | Remarks | FO Comment
ELECTRICAL |  |  |  |  | Wish List |  | Interval Recommended by the Code (Months)
| EL-EQUIP-HV (Over 750V) |  | Thermal Scanning in RFP | Recommendation from PM Team - Interval (Months) | 1. Good to have | 2. Have to | Recommendation from PM Team | Minimum | Good Practice | Optimized | Thermal Scanning Requirement (As per CSA Z463-18 Maintenance of Electrical System)
| EL-EQUIP-PDGPB | Power Distribution Switchgear and panel boards | √ | 12 |  | √ | 12 | 24 | 12 | 12 | Yes | Annual (If applicable) | PDGPB | MUMUN, WHMSC (13KV)
| EL-EQUIP-TX-LQ | Power Transformer (Liquid Filled) | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual (If applicable) | TX-LQ |  | mostly bi-annual
| EL-EQUIP-TX-DRY | Power Transformer (Dry-type) | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual (If applicable) | TX-DRY |  | mostly bi-annual
| EL-EQUIP-CA | Power Cables | √ | 6 |  | √ (Junction Panel Connection) | 6 | 12 | 12 | 6 | Yes | Annual | CA |  | Need to define power cables (suggest all MV cables and feeders greater than 400A)
| EL-EQUIP-HVCB | High voltage power circuit breaker | √ | 12 |  | √ | 12 | 36 | 12 | 12 | Yes | Annual (If applicable) | CB-HV |  | Mostly tri-annual
EL-EQUIP-LV (30V - 750V)
| EL-EQUIP-PDGPB | Power Distribution Switchgear and panel boards | √ | 12 |  | √ | 12 | 24 | 12 | 12 | Yes | Annual | PDGPB
| EL-EQUIP-TX-LQ | Power Transformer (Liquid Filled) | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual | TX-LQ
| EL-EQUIP-TX-DRY | Power Transformer (Dry-type) | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual | TX-DRY
| EL-EQUIP-CA | Power Cables | √ | 6 |  | √ (Junction Panel Connection) | 6 | 12 | 12 | 6 | Yes | Annual | CA |  | Need to define power cables (suggest all MV cables and feeders greater than 400A)
| EL-EQUIP-MEB | Metal-enclosed busways | √ | 12 |  | √ (Busbar connection in main panel, junction fittings and etc.) | 12 | 24 | 12 | 12 | Yes | Annual | MEB |  | Combine with PDGPB
| EL-EQUIP-DS | Disconnect Switch & Circuit Switcher | √ | 12 |  | √ | 12 | 36 | 12 | 12 | Yes | Annual | DS |  | Combine with PDGPB
| EL-EQUIP-MCCB | Circuit Breaker (Insulated & Moulded case) | √ | 12 |  | √ | 12 | 36 | 12 | 12 | Yes | Annual | MCCB
| EL-EQUIP-LVCB | Low voltage power circuit breaker | √ | 12 |  | √ | 12 | 36 | 12 | 12 | Yes | Annual | CB-LV
| EL-EQUIP-MD | Protection, Control and Metering devices | √ | 12 | √ |  | 12 |  |  |  | Not mention, should cover in MCC | Annual | MD |  | Combine with PDGPB
| EL-EQUIP-TX-CT | Instrument Transformer - CTs | √ | 12 |  | √ | 12 | 18 | 12 | 12 | Yes | Annual | CT |  | Combine with PDGPB
| EL-EQUIP-TX-VT | Instrument Transformer - VTs | √ | 12 |  | √ | 12 | 18 | 12 | 12 | Yes | Annual | VT |  | Combine with PDGPB
| EL-EQUIP-MOTOR | Motors (Rotating Machine & Pumps) | √ | 3 |  | √ (Rotating Part) | 3 | 12 | 6 | 3 | Yes | Annual | MOTOR |  | greater than 200Hp??
| EL-EQUIP-MCC | Motor Control Centers (MCC) | √ | 12 |  | √ (Conduct while has electrical load) | 12 | 24 | 12 | 12 | Yes | Annual | MCC
| EL-EQUIP-DC | DC Battery System |  | - | [6 empty] | Not mention | Annual (If applicable) | DC |  | Move the HV Equipment, combine with PDGPB
| EL-EQUIP-VFD | Variable Frequency Drive | √ | 36 |  | √ | 36 | - | 60 | 36 | Yes (while running and have load) | Annual (If applicable) | VFD | Existed in EAM 11.4 now
| EL-EQUIP-MVMS | Medium voltage motor starters | √ | 12 | √ |  | 12 |  |  |  | Not mention, should cover in MCC | Annual (If applicable) | MVMS
| EL-EQUIP-SA | Surge Arrestor | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual (If applicable) | SA |  | Combine with PDGPB and MCC
| EL-EQUIP-CAP | Capacitors (Power Factor Correction), e.g. WHMSC, EOC, MUMUN | √ | 3 |  | √ | 3 | 12 | 6 | 3 | Yes | Annual (If applicable) | CAP |  | Combine with PDGPB and MCC
| EL-EQUIP-REA | Reactors (Power Factor Correction) | √ | 3 |  | √ | 3 | 12 | 6 | 3 | Yes | Annual (If applicable) | CAP |  | Combine with PDGPB and MCC
| EL-EQUIP-UPS | Uninterruptable Power Supply | √ | 12 |  | √ | 12 | 12 | 12 | 12 | Yes (Static small and large unit, while running and have load) | Annual (If applicable) | UPS | Existed in EAM 11.4 now | suggest removal - no need for small UPS systems. IT manages large UPS systems
| EL-EQUIP-SCADA | SCADA (For Future CCOM onboarding) | √ | 12 | √ |  | 12 |  |  |  | Not mention | Annual (If applicable) | SCADA |  | Suggest removal - no scada systems (BMS)
| EL-EQUIP-EG | Emergency Generator | √ | 6 |  | √ | 6 | - | 12 | 6 | Yes
| EL-EQUIP-ATS | Automatic Transfer Switch | √ | 12 |  | √ | 12 | 12 | 12 | 12 | Yes
| EL-EQUIP-CPLUG | Parking Car Plugs |  | - | [6 empty] | Not mention | Annual (If applicable) | CPLUG | Existed in EAM 11.4 now
EL-ELV (Not exceed 30V)
| EL-ELV-PA | Public Address System |  | - | [6 empty] | Not mention | Annual (If applicable) | PA |  | suggest removal
| EL-ELV-SSS | Surveillance and Security System (CCTV, Access Control System) |  | - | [6 empty] | Not mention | Annual (If applicable) | SSS |  | suggest removal
EL-SYS
| EL-SYS-GB | Grounding and Bonding Systems |  | - | [6 empty] | Not mention | Annual | GB |  | Combine with PDGPB(Both HV and LV)
| EL-SYS-GFPS | Grounding Fault Protection Systems | √ | 12 |  | √ |  |  |  |  | Not mention, should cover in Switchgear panel | Annual | GFPS
| EL-SYS-LP | Lightning Protection Systems |  | - | [6 empty] | Not mention | Annual (If applicable) | LP
| EL-EVS | Electric Vehicle Equipment |  | - | [6 empty] | Not mention | Annual (If applicable) | EVS
EL-PDM
| EL-PDM-IR | Infrared Scanning and Thermography (PdM) |  | - | [6 empty] | N/A | If applicable | IR |  | We need to discuss the standard for EAM with these and what is the best way to issue these PM's
| EL-PDM-UI | Ultrasound Inspection (PdM) |  | - | [6 empty] | N/A | If applicable | US
| EL-PDM-VA | Vibration Analysis for Rotating Machines (PdM) |  | - | [6 empty] | N/A | If applicable | VA

## Chiller List
| Address | Quantity | Manufacturer | Model # | Oil Replacement in Maint Manual | Chiller Desciption | Annual Cost
+15 Admin to Police | 316 y - 7 AVE SE | 1 | McQuay (Daikin) | AGZ010Bs712-ER10 | Annual Acid test oil sample | Air Cooled Packaged Chiller, 10 Tons | 0
Alberta Trade Center | 315 - 10 AVE SE | 1 | York | YLAA0135SE28XAA | Annual Sample Compressor Oil, check for Acid, and replace if necessary. | Chiller, Air Cooled, Scroll, 101-140 Tons | 0
Andrew Davison Building | 133 - 6 AVE SE | 1 | York | YMC2-S1097AAS | Not Applicable, Oil Free. | Chiller, Water Cooled, Magnetic Bearing Centrifugal, 250-450 Tons | 0
Corporate Warehouse | 2340 - 22 ST NE | 1 | Technical System | 30AOLD26-FC |  | Air Cooled Packaged Chiller, 30 Tons | 0
Emergency Operations Center | 673 - 1 ST NE | 4 | Trane | RTWD 110G 2B02 | Have a qualified laboratory perform an oil analysis to determine system moisture content and acid level annually | Water Cooled Rotary Liquid Chiller (110 Ton, Dual compressor & circuit) | 0
Emergency Operations Center | 673 - 1 ST NE | 1 | Trane | RTWD 130G 2B02 | Have a qualified laboratory perform an oil analysis to determine system moisture content and acid level annually | Water Cooled Rotary Liquid Chiller (130 Ton, Dual compressor & circuit) | 0
Fire Station #06 | 360 - 8 ST SW | 1 | Carrier (Daikin) | AGZ029BS712-ER10 | Annual Acid test oil sample | Air Cooled Water Chiller Unit | 0
Municipal Building | 800 MACLEOD TR SE | 3 | York | YTK1K1E2CTA | Perform oil analysis on compressor lube oil Annually | Chiller, Water Cooled, Low Pressure Centrifugal, 450-799 Tons | 0
Municipal Building | 800 MACLEOD TR SE | 1 | Daikin | WMC048SDSNA | Not Applicable, Oil Free. | Water cooled, magnetic bearing centrifugal compressor | 0
Public Building | 205 - 8 AVE SE | 1 | Multistack | MS50X6A2W1-R410A | Not mention. Subject to oil test resuly annually is recommended | Chiller, Water Cooled, Modular (50 Tons) | 0
Ralph Klein Pk Interpr Ctr | 12350 - 84 ST SE | 1 | ENG Air | DX | Not sufficient Info, Model no. is required to get more info. Subject to oil test resuly annually is recommended | R410A Refrigerant | 0
Sarcee Administration Building | 110 WESTHILLS WAY SW | 1 | Carrier | 30RAP080 | Obtain and test an oil sample annually. Change oil only if necessary. | Air Cooled Chiller, 80 Tons | 0
The following to start January 2022
Village Square Leisure Center | 2623 - 56 St NE | 1 | York | YKC3CQQ4-CJ65 | Perform oil analysis on compressor lube oil Annually | Chiller, R134a Refrigerant, 260 Ton | 0
Manchester Building U | 677 - 25 AVE SE | 1 | York | YLAA 0090-SE-28-XAA | Annual Sample Compressor Oil, check for Acid, and replace if necessary. | Air Cooled Scroll Chiller, 90 Tons | 0
Manchester Building E | 2808 SPILLER RD SE | 1 | York | YCAV-0227-PS-58-VACCST | Annual Sample Compressor Oil, check for Acid, and replace if necessary. | Air Cooled Screw Liquid Chiller, 211 Tons | 0
Water Center | 651 - 25 AVE SE | 1 | McQuay (Daikin) | AGS-170-CM-37-ER-10 | Annual Acid test oil sample | Air Cooled Screw Chiller, 176 Tons | 0

## RC-DA-01
RC-DA-01 | ANNUAL AMMONIA DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CSA B52, OHS & ABSA requirement for inspection & calibration if app
30 | Notify alarm monitoring company to place system on test
40 | Check the condition of permanent sign for the refrigeration system that indicates the following:
50 | Name and address of installer;
60 | Refrigerant type;
70 | Lubricant type and amount;
80 | Total weight of refrigerant required for normal operation;
90 | Field test pressures applied;
100 | Refrigeration capacity at design or nominal conditions; and
110 | For prime mover(s), the rating in kilowatts (hp) or full-load current and voltage
120 | Check condition of machinery room
130 | Start ventilation and actuate an alarm at the lowest practical detection levels not exceeding 300 ppm
140 | Check the function of gas detector
150 | Check pressure relief valve and over pressure protection safety device. Re-certify or replace as needed
160 | Test all pressure limiting device for set point accuracy
170 | Test the leak detectors for function at the specified refrigerant concentration
180 | Check the audible and visible alarm and interlock with ventilation
190 | Inspect all refrigerant lines, vent lines for vibration and damages
200 | Ensure emergency procedures and instructions are in place
210 | Record observations as follows: Ammonia Virtual Alarm Test
220 | 100 ppm - Office Horn activated
230 | 100 ppm - Exhaust Fan energized
240 | 100 ppm - Make-up Air Unit energized
250 | 100 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
260 | 300 ppm - Office Horn activated
270 | 300 ppm - Blue Strobe activated
280 | 300 ppm - Exhaust Fan energized
290 | 300 ppm - Make-up Air Unit energized
300 | 300 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
310 | Inspect, verify and record operation of switching indicated below:
320 | REFRIGERATION ROOM VESTIBULE SWITCHING
330 | Test occupied switch and energizes exhaust fan and make-up air unit.
340 | Activate blue strobe light and office horn
350 | Verify alarm signal to monitoring company
360 | Verify BAS display in agreement with tests
370 | Perform a 300 ppm gas test on the NH3 sensor and calibrate as needed
380 | SENSOR CALIBRATION. Record observation below - Allowable error: +/- 5% ppm (NH3)
390 | BEFORE CALIBRATION - Actual Reading
400 | BEFORE CALIBRATION - BAS Reading
410 | POST CALIBRATION - Actual Reading
420 | POST CALIBRATION - BAS Reading
430 | Verify LCD display read out for ammonia sensor located on the vestibule Panel if equipped
440 | Record observation below - Allowable error: +/- 5% ppm (NH3)
450 | Record LCD Panel Reading:
460 | Notify alarm monitoring company to take system off test
Existing task in EAM
Sequence | Description
10 | NOTIFY ALARM MONITORING COMPANY TO PLACE SYSTEM ON TEST
20 | Generate virtual 100ppm & 300ppm alarm signals to test program sequence of
30 | operation of detection system:
40 | 1st Stage (100 ppm) and 2nd Stage (300 ppm) ammonia alarms
50 | Generate Stage 1 alarm, 100 ppm or greater ammonia concentration, the first
60 | stage of the alarm system is activated and a horn begins to sound in the office
70 | area. Ventilation unit and exhaust fan are energized. Dialer sends alarm signal
80 | to monitoring company.
90 | Generate Stage 2 alarm, 300 ppm or greater ammonia concentration, the second
100 | stage of the alarm system is activated and a horn begins to sound in the office
110 | area. A blue strobe light is activated outside the compressor room. Ventilation
120 | unit and exhaust fan are energized at high level. Equipment runs until ammonia
130 | level has dropped below 50 ppm for 120 seconds. Dialer sends alarm signal to
140 | monitoring company.
150 | Record observations as follows: Ammonia Virtual Alarm Test
160 | 100 ppm - Office Horn activated
170 | 100 ppm - Exhaust Fan energized
180 | 100 ppm - Make-up Air Unit energized
190 | 100 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
200 | 300 ppm - Office Horn activated
210 | 300 ppm - Blue Strobe activated
220 | 300 ppm - Exhaust Fan energized
230 | 300 ppm - Make-up Air Unit energized
240 | 300 ppm - Exhaust Fan, Make-up Air Unit and Horn de-energized below 50 ppm
250 | Inspect, verify and record operation of switching indicated below:
260 | REFRIGERATION ROOM VESTIBULE SWITCHING
270 | Occupied Switch ON/OFF Energizes/de-energizes exhaust fan and make-up air unit.
280 | Emergency Ventilation Switch Energizes (START ONLY) exhaust fan and make-up
290 | air unit at maximum volume, as well as blue strobe light and office horn. Alarm
300 | signal sent to monitoring company.
310 | REFRIGERATION ROOM SWITCHING (AT ROOM EXITS)
320 | Emergency Ventilation Switch - START / STOP
330 | Vestibule Occupied switch Passed?
340 | Vestibule Emergency ventilation switch Passed?
350 | Refrigeration Room manual switch exit 1 Passed?
360 | Refrigeration Room manual switch exit 2 Passed?
370 | Verify all alarm signals received by monitoring company Passed?
380 | Verify BAS display in agreement with tests Passed?
390 | 1. Replace ammonia element in NH3 sensor
400 | 2. Perform a 300 ppm gas test on the NH3 sensor and calibrate as below (Passed?)
410 | SENSOR CALIBRATION. Record observation below - Allowable error: +/- 5% ppm (NH3)
420 | BEFORE CALIBRATION - Actual Reading
430 | BEFORE CALIBRATION - BAS Reading
440 | POST CALIBRATION - Actual Reading
450 | POST CALIBRATION - BAS Reading
460 | 3. Verify LCD display read out for ammonia sensor located on the vestibule Panel
470 | Record observation below - Allowable error: +/- 5% ppm (NH3)
480 | LCD Panel Reading:
490 | NOTIFY ALARM MONITORING COMPANY TO TAKE SYSTEM OFF TEST

## PLSE-NH3-A-01
PLSE-NH3-A-01 | ANNUAL AMMONIA PERSONAL DETECTOR SET CALIBRATION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | ****Personal NH3 Detector****
30 | Ensure detector is free of physical damage and obstruction, replace if necessary
40 | Calibrate the detector according to manufacturer's specifications
50 | Adjust the detector response to match the desired value
60 | And compared to a known traceable concentration of test gas
70 | Check the detector battery condition, replace if necessary
80 | Check the detector sensor condition, replace if necessary
90 | Check the detector dust and water filter condition, replace if necessary
100 | ****Docking Station****
110 | Inspect the docking station condition, clean as required
120 | Check that hoses and tubing are secure
130 | Check hoses & tubing for damage to prevent escapes of gas, replace if necessary
140 | Inspect visually the modules and detector seals, replace if dirty or damaged
150 | Check all cable connections are secure
160 | Check the sealing insert condition, replace if necessary
170 | Check the fresh air filter, replace if necessary
180 | ****Gas Canister****
190 | Check gas canister condition and capacity, replace w/ full capacity as required
200 | ****Regulator****
210 | Ensure canister regulator is free of damage and obstruction, replace if needed
220 | Check the pressure gauge operation and settings during calibration
230 | *************************************************
240 | Note and record all calibration steps and results in a report
250 | Findings reported to Facility Maintenance Coordinator

## BMS-NH3-A-02
BMS-NH3-A-02 | ANNUAL AMMONIA SENSOR REPLACEMENT
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Order and install 15 LPT-NH3 0-500 ppm Ammonia sensors
30 | Once installed, test the system for operation
40 | Findings Reported To Building Automation (EMCS) Leader

## BMS-NH3-A-01
BMS-NH3-A-01 | ANNUAL AMMONIA SENSOR CALIBRATION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Calibrate Ammonia (NH3) sensor
30 | Test the operational sequence
40 | Findings Reported To Building Automation (EMCS) Leader

## LS-ELEV-ER-Q
LS-ELEV-ER-Q | QUARTERLY ELEVATOR RECALL INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to National Fire Code (Section 7.2.2) & Elevating Device Codes Regulation AR 62/2009 requirement for inspection
30 | Test the Firefighters Emergency Operation (FEO) recall function by bldg fire alarm system
40 | Test the function of in-car emergency switches
50 | Test the manual key-operated recall switches located outside elevator shaft
60 | Test the function of automatic emergency recall system
70 | If no fire alarm system, test the recall function with detectors in machine room and lobbies
80 | Record any deficiencies in log book and correct immediately.

## LS-OPENINGS-EML
LS-OPENINGS-EML | ANNUALLY ELECTROMAGNETIC LOCK INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NBC 2019 Standard - Section 3.4.6.16 requirement for inspection
30 | Do not incorporate latches, pins or other similar devices to keep the door in the closed position
40 | Test release upon actuation of the alarm signal from the building’s fire alarm system
50 | Test release upon loss of its power supply and of power to its auxiliary controls
60 | Test release upon actuation of the manual station installed within 0.5 m of door with auxiliary contact
70 | The electromagnetic lock requires manual resetting upon release
80 | A legible sign with the words “EMERGENCY EXIT UNLOCKED BY FIRE ALARM" mounted on door
90 | Emergency lighting is provided at the doors.
100 | Test the function of by-pass switch (if applicable)
110 | Findings Reported To Maintenance Supervisor

## LS-SD-M
ANNUALLY SMOKE DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 72 - Chapter 14 requirement for inspection
30 | Inspect and clean detectors
40 | Calibrate Detectors
50 | Carry out functional test as per manufacturer's instruction
60 | Press the test buttons for 5 seconds to test the sound operation and flashing LED light or
70 | Test operation with aerosol tester
80 | Verify location and condition
90 | Verify operation of audible and visual alarms and signal
100 | Inspect lithium batteries for corrosion and tightness of connection (if applicable)
110 | Replace 9V battery for smoke detector (if applicable)
120 | Check the expiry date for smoke detector, replace after 10 years
130 | Check ULC marking for any new detectors
140 | Findings Reported To Maintenance Supervisor
Existing task in EAM (SD-01) - COC Annual Smoke Detector Inspection
Sequence | Description
10 | Check The Keys Within The Lock Boxes To Ensure That They Are Correct
20 | Make Sure Keys Will Allow Emergency Responders Access Into The Facility
30 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
40 | Pre Job Hazard Assessment Completed?

## LS-SD-S
LS-SD-S | SEMI-ANNUALLY SMOKE DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 72 - Chapter 14 (14.3.1) requirement for inspection
30 | Carry out visual inspection todetectors
40 | Inspect and clean detectors
50 | Verify the detectors are mounted properly
60 | Verify location and condition
70 | Findings Reported To Maintenance Supervisor

## SAFETY-FPS-SRD
SAFETY-FPS-SRD-A | ANNUALLY SELF RETRACTING DEVICE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Approved by CSA Standard Z259.2.2-98, Self-Retracting Devices for Personal Fall-Arrest Systems
30 | Must be inspected by worker before it is used on each shift
40 | Keep free from substance and condition to avoid deterioration of equipment
50 | Re-certified as specified by manufacturer if needed
60 | Anchored above the worker's head
70 | Minimizes the hazard of swinging and limits the swing drop distance to 1.2 Metres if worker falls
80 | Findings Reported To Maintenance Supervisor

## SAFETY-FPS-FA
SAFETY-FPS-FA-Q-01 | ANNUALLY FALL ARRESTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Fulfill CSA Standard Z259.2.1-98 (R2004), Fall Arresters, Vertical Lifelines, and Rails,
30 | Fulfill ANSI/ASSE Standard Z359.1-2007, Safety requirements for personal fall arrest systems, subsystems and components
40 | Fall arrestor must be inspected by worker before it is used on each shift
50 | Keep free from substance and condition to avoid deterioration of equipment
60 | Re-certified as specified by manufacturer if needed
70 | Remove from service if it is defective, contact with heat, chemical and any substance that may corrode
80 | Remove from service after personal fall arrestor system has stopped a fall
90 | Do not return to use unless a professional engineer or manufacturer certifies the system is safe
100 | Findings Reported To Maintenance Supervisor

## Allied LS Cost
Zone | PO# | PO value | Current Invoice | Previous Invoices (Starting June 2023) | [5 empty] | Total Invoiced Amounts |  | Current Variance (Remaining PO Value)
Centre | 880247A | 163000 | 660 | 2310 | [5 empty] | 2970 |  | 160030 |  |  | 98.18% | done for Oct |  |  |  | 8417
NE | 880334A | 145000 | 5810 | 20272 | [5 empty] | 26082 |  | 118918 |  |  | 82.01% |  |  |  |  | 57133.73
NW | 880335A | 150000 | 7136 | 53544.73 | [5 empty] | 60680.73 |  | 89319.27 |  |  | 59.55% |  |  |  |  | 65550.73
SE | 880333A | 310000 | 13292 | 59069.48 | [5 empty] | 72361.48 |  | 237638.52 |  |  | 76.66%
SW | 880332A | 153000 | 6664 | 37709.37 | [5 empty] | 44373.37 |  | 108626.63 |  |  | 71%
|  | 921000 | 33562 | 172905.58 | [5 empty] | 206467.58 |  | 714532.42 |  |  | 77.58%
|  |  | Invoice Date: October 31, 2023 (Oct billings) | [6 empty] | Fire Alarm | [8 empty] | Sprinkler | [12 empty] | Emergency Lights | [8 empty] | Ventilation Hood Suppression |  |  |  | Total PO Value | Total Invoiced
[10 empty] | Annual Inspection |  |  |  | Monthly Inspection |  |  |  | Total Billings | Annual Inspection |  |  |  | Quarterly Inspection |  |  |  | Monthly Inspection |  |  |  | Total Billings | Annual Inspection |  |  |  | Monthly Inspection |  |  |  | Total Billings | Semi-Annual Inspection |  |  | Total Billings
City of Calgary PO # | PO Line # | Department | Facility Name as per Allied | Building Inventory List Name | Fund | Dept ID | Activity | Reference | Zone | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Annual Inspection Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Monthly Inspection Billings | Total Fire Alarm Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Annual Inspection Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Quarterly Inspection Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Monthly Inspection Billings | Total Sprinkler Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Annual Inspection Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Monthly Inspection Billings | Total Emergency Light Billings | Inspection Complete | City of Calgary Work Order # | Quoted Amount | Total Ventilation Hood Suppression Billings
0000880247A | 1-1 | City Core | Alberta Trade Centre | ALBERTA TRADE CENTRE | 20 | 12438 | 201535 | 11673CP000 | Centre |  |  | 2957 | 0 |  |  | 45 | 0 | 0 |  |  | 440 | 0 | Yes | 3517067 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 2678 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 7920 | 330
0000880247A | 1-1 | City Core | Andrew Davison | ANDREW DAVISON | 20 | 12438 | 201535 | 11718CP000 | Centre |  |  | 9233 | 0 |  |  | 45 | 0 | 0 |  |  | 1100 | 0 |  |  | 550 | 0 |  |  | 45 | 0 | 0 |  |  | 2869 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 15707 | 0
0000880247A | 1-1 | City Core | Calgary Public Building | CALGARY PUBLIC BUILDING | 20 | 12438 | 201535 | 11680CP000 | Centre |  |  | 4511 | 0 |  |  | 45 | 0 | 0 |  |  | 440 | 0 | Yes | 3517315 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 3182 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 9978 | 330
0000880247A | 1-1 | City Core | City Hall Administration Building | CITY HALL ADMINISTRATION BUILDING | 20 | 12438 | 201535 | 15007CP000 | Centre |  | 3436315 | 15234 | 0 |  |  | 45 | 0 | 0 |  | 3436315 | 1380 | 0 |  | 3395041 3519373 | 1250 | 0 |  |  | 45 | 0 | 0 |  | 3436312 | 1684 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 22903 | 0
0000880247A | 1-1 | City Core | Historic City Hall | HISTORIC CITY HALL | 20 | 12438 | 201535 | 11697CP000 | Centre |  | 3436331 | 7681 | 0 |  |  | 45 | 0 | 0 |  | 3436331 | 840 | 0 |  | 3519444 | 840 | 0 |  |  | 45 | 0 | 0 |  | 3436327 | 863 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 12759 | 0
0000880247A | 1-1 | City Core | Historic Fire Hall 01 | HISTORIC FIRE HALL #1 | 20 | 12438 | 201546 | 11725FM000 | Centre |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3435718 | 623 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 623 | 0
0000880247A | 1-1 | City Core | Historic Fire Hall 01 Garage | HISTORIC FIRE HALL #1 GARAGE | 20 | 12438 | 201546 | 11728FM000 | Centre |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 187 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 187 | 0
0000880247A | 1-1 | City Core | Municipal Building | MUNICIPAL BUILDING | 20 | 12438 | 201535 | 11696CP000 | Centre |  | 3436351 | 65379 | 0 |  |  | 45 | 0 | 0 |  | 3436390 | 3100 | 0 |  | 3436391 | 2095 | 0 |  |  | 45 | 0 | 0 |  | 3436383 | 4487 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 80106 | 0
0000880334A | 1-1 | FM | Ad Valorem | AD VALOREM PLACE | 20 | 12439 | 201535 | 15040CP000 | NE |  |  | 4186 | 0 | Yes | 3517025 | 45 | 45 | 45 |  |  | 900 | 0 | YES | 3393147 3517040 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 1108 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 8039 | 375
0000880334A | 1-1 | CFD | Apparatus Repair Shop | APPARATUS REPAIR SHOP | 20 | 12439 | 201536 | 16539FM000 | NE |  |  | 2143 | 0 | Yes | 3524439 | 45 | 45 | 45 |  |  | 550 | 0 |  | 3437119 | 220 | 0 | Yes | 3524448 | 45 | 45 | 45 |  |  | 751 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 5094 | 90
0000880334A | 1-1 | CFD | Apparatus Spare | SPARE APPARATUS SHOP | 20 | 12439 | 201536 | 16538FM000 | NE |  |  | 1187 | 0 | Yes | 3525341 | 45 | 45 | 45 |  |  | 0 | 0 |  | 3437832 | 220 | 0 | Yes | 3525348 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2702 | 90
0000880334A | 1-1 | FM | Corporate Warehouse | CORPORATE WAREHOUSE | 20 | 12439 | 201535 | 16496CP000 | NE |  |  | 2988 | 0 | Yes | 3517355 | 45 | 45 | 45 |  |  | 800 | 0 | Yes | 3393498 3517405 | 220 | 220 |  |  | 45 | 0 | 220 |  |  | 2099 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 7402 | 265
0000880334A | 1-1 | CFD | Emergency Operations Centre | EMERGENCY OPERATIONS CENTRE | 20 | 12439 | 201538 | 17567FM000 | NE |  |  | 2762 | 0 | Yes | 3524463 | 45 | 45 | 45 |  |  | 5900 | 0 |  | 3437158 | 4500 | 0 | Yes | 3524526 | 45 | 45 | 45 |  |  | 867 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 23884 | 90
0000880334A | 1-1 | FM | EMS Station 4 | EMS #4 | 20 | 12439 | 204065 | 11775CP000 | NE | Yes | 3524412 | 1037 | 1037 |  |  | 90 | 0 | 1037 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3524420 | 233 | 233 |  |  | 0 | 0 | 233 |  |  | 0 | 0 | 2260 | 1270
0000880334A | 1-1 | FM | Fire Station #32 - Saddle Ridge Emerg. Resp. Ctr | SADDLE RIDGE EMERGENCY RESPONSE CENTRE | 20 | 12439 | 201536 | 17067FM000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3474806 | 250 | 250 | 500 | 250
0000880334A | 1-1 | Rec | McCall Lake Golf Club | MCCALL LAKE CLUBHOUSE | 20 | 12439 | 201539 | 11798FM000 | NE |  |  | 562 | 0 | Yes | 3523511 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 284 | 0 | Yes | 3523535 | 48 | 48 | 48 |  |  | 250 | 0 | 2864 | 138
0000880334A | 1-1 | Parks | Northern Hills Depot | NORTHERN HILLS DEPOT | 20 | 12439 | 201537 | 15091FM000 | NE |  |  | 1342 | 0 | Yes | 3523930 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397586 | 251 | 0 |  | 3523517 | 0 | 0 | 0 |  |  | 0 | 0 | 2583 | 90
0000880334A | 1-1 | Parks | Prairie Winds Depot | PRAIRIE WINDS DEPOT | 20 | 12439 | 201537 | 12189FM000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 119 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119 | 0
0000880334A | 1-1 | Parks | Prairie Winds Spray Park Mech Bldg | PRAIRIE WINDS SPRAY PARK MECH BUILDING | 20 | 12439 | 201537 | 30016FM000 | NE |  |  | 828 | 0 |  |  | 45 | 0 | 0 |  |  | 550 | 0 |  |  | 220 | 0 |  |  | 45 | 0 | 0 |  |  | 135 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3028 | 0
0000880334A | 1-1 | Parks | Prairie Winds Wading Pool Mech Bldg and Comfort Station | PRAIRIE WINDS WADING POOL MECH BUILDING AND WASHROOM | 20 | 12439 | 201537 | 12183FM000 | NE |  |  | 0 | 0 |  | 3524221 | 0 | 0 | 0 |  |  | 0 | 0 |  | 3478951 | 0 | 0 |  | 3524226 | 0 | 0 | 0 |  |  | 378 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 378 | 0
0000880334A | 1-1 | Rec | Renfrew Aquatic | RENFREW AQUATIC & RECREATION CENTRE | 20 | 12439 | 201539 | 15155FM000 | NE |  |  | 1199 | 0 | Yes | 3523058 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 727 | 0 | Yes | 3523064 | 126 | 126 | 126 |  |  | 0 | 0 | 4302 | 216
0000880334A | 1-1 | FM | Roads Edmonton Trail | EDMONTON TRAIL DEPOT MODULAR OFFICE | 20 | 12439 | 201536 | 20021FM000 | NE |  |  | 735 | 0 | Yes | 3525372 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1725 | 90
0000880334A | 1-1 | Parks | Rotary Park Comfort Stn | ROTARY PARK CHANGE ROOM & WASHROOM | 20 | 12439 | 201537 | 12495FM000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 142 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 142 | 0
0000880334A | 1-1 | Parks | Saddle Ridge Depot | SADDLE RIDGE DEPOT | 20 | 12439 | 201537 | 20020FM000 | NE |  |  | 374 | 0 | Yes | 3524025 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397702 | 287 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1651 | 90
0000880334A | 1-1 | FM | Saddle Ridge Lunchroom Trailer | SADDLE RIDGE LUNCHROOM TRAILER | 20 | 12439 | 201540 | 15045RD000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396267 | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 292 | 0
0000880334A | 1-1 | Parks | Saddle Ridge Quonset | SADDLE RIDGE DEPOT QUONSET | 20 | 12439 | 201537 | 12211FM000 | NE |  |  | 432 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397709 | 196 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1618 | 90
0000880334A | 1-1 | FM | Spring Gardens Building B | SPRING GARDENS BUILDING B | 20 | 12439 | 201535 | 11815CP000 | NE |  |  | 1884 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 787 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3661 | 90
0000880334A | 1-1 | FM | Spring Gardens Building D | SPRING GARDENS BUILDING D | 20 | 12439 | 201535 | 11821CP000 | NE |  |  | 864 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 816 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2670 | 90
0000880334A | 1-1 | FM | Spring Gardens Building E | SPRING GARDENS RESOURCE RECOVERY BUILDING E | 20 | 12439 | 201540 | 11816WR000 | NE |  |  | 1092 | 0 | Yes |  | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3396121 3520988 | 220 | 220 |  | 3521008 | 45 | 0 | 220 |  |  | 700 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3527 | 265
0000880334A | 1-1 | FM | Spring Gardens Building G | SPRING GARDENS BUILDING G | 20 | 12439 | 201540 | 11811RD000 | NE |  |  | 1843 | 0 | Yes | 3521043 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1575 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4408 | 90
0000880334A | 1-1 | FM | Spring Gardens Building G1 | SPRING GARDENS BUILDING G1 | 20 | 12439 | 201540 | 12157RD000 | NE |  |  | 0 | 0 | Yes | 3521234 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 117 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1107 | 90
0000880334A | 1-1 | FM | Spring Gardens Building O | SPRING GARDENS BUILDING O | 20 | 12439 | 201540 | 16206RD000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880334A | 1-1 | FM | Spring Gardens Building P | SPRING GARDENS BUILDING P | 20 | 12439 | 201540 | 15034RD000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880334A | 1-1 | Parks | Spring Gardens Pk Building A | SPRING GARDENS PARKS BUILDING A | 20 | 12439 | 201537 | 11813FM000 | NE |  |  | 741 | 0 | Yes | 3524363 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 133 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1864 | 90
0000880334A | 1-1 | FM | Spring Gardens South Building R | SPRING GARDENS SOUTH BUILDING R | 20 | 12439 | 201535 | 31486FM000 | NE |  |  | 621 | 0 | Yes | 3521255 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3396254 3521259 | 220 | 220 |  | 3521267 | 45 | 0 | 220 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2466 | 265
0000880334A | 1-1 | CFD | Station 22 | FIRE STATION #22 | 20 | 12439 | 201536 | 11827FM000 | NE |  |  | 1380 | 0 | Yes | 3524800 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2370 | 90
0000880334A | 1-1 | CFD | Station 38 | FIRE STATION #38 | 20 | 12439 | 201536 | 30033XX000 | NE |  |  | 460 | 0 | Yes | 3524993 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3437551 | 330 | 0 | Yes | 3524996 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2635 | 90
0000880334A | 1-1 | CFD | Station 4 | FIRE STATION #4 | 20 | 12439 | 201536 | 11774FM000 | NE |  |  | 1128 | 0 | Yes | 3525171 | 45 | 45 | 45 |  |  | 460 | 0 | Yes | 3525175 | 330 | 330 |  |  | 45 | 0 | 330 |  | 3397240 | 471 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3904 | 375
0000880334A | 1-1 | CFD | Station 44 | FIRE STATION #44 | 20 | 12439 | 201536 | 31535FM000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397192 | 311 | 0 |  |  | 0 | 0 | 0 |  | 3437649 | 250 | 0 | 811 | 0
0000880334A | 1-1 | Rec | Stew Hendry (Henry Viney Arena) | STEW HENDRY ARENA | 20 | 12439 | 201539 | 15161FM000 | NE |  |  | 629.5 | 0 | Yes | 3522224 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 300 | 0 | Yes | 3522225 | 107 | 107 | 107 |  |  | 0 | 0 | 3096.5 | 197
0000880334A | 1-1 | Rec | Henry Viney Arena (Stew Hendry) | HENRY VINEY ARENA | 20 | 12439 | 201539 | 15154FM000 | NE |  |  | 629.5 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 300 | 0 | Yes | 3522427 | 107 | 107 | 107 |  |  | 0 | 0 | 2106.5 | 107
0000880334A | 1-1 | CFD | Temporary Fire Station #27 | TEMPORARY FIRE STATION #27 | 20 | 12439 | 201536 | 31153XX000 | NE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  | 3525237 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3525373 | 250 | 250 | 500 | 250
0000880334A | 1-1 | Rec | Village Square Leisure Centre | VILLAGE SQUARE LEISURE CENTRE | 20 | 12439 | 201539 | 11785FM000 | NE |  |  | 4274 | 0 | Yes | 3523737 | 45 | 45 | 45 |  |  | 660 | 0 |  | 3481336 | 440 | 0 | Yes | 3523780 | 45 | 45 | 45 |  |  | 2466 | 0 | Yes | 3523750 | 397 | 397 | 397 |  |  | 250 | 0 | 14442 | 487
0000880334A | 1-1 | FM | Whitehorn Multi Services | WHITEHORN MULTI-SERVICES CENTRE | 20 | 12439 | 201535 | 11808CP000 | NE |  |  | 9866 | 0 | Yes | 3521721 | 45 | 45 | 45 |  |  | 2680 | 0 |  | 3437070 | 330 | 0 | Yes | 3521782 | 45 | 45 | 45 |  |  | 1024 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 15415 | 90
0000880335A | 1-1 | Parks | 19 St Depot | 19 ST DEPOT | 20 | 12439 | 201537 | 15088FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397496 | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Parks | Baker Park Comfort Station | BAKER PARK WASHROOM | 20 | 12439 | 201537 | 12176FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397632 | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880335A | 1-1 | Parks | Baker Park Depot | BAKER PARK DEPOT | 20 | 12439 | 201537 | 31004FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397530 | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Parks | Baker Park Garage | BAKER PARK GARAGE | 20 | 12439 | 201537 | 31005FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 113.84 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 113.84 | 0
0000880335A | 1-1 | FM | Bearspaw Cold Storage | BEARSPAW COLD STORAGE | 20 | 12439 | 201540 | 11844RD000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 292 | 0
0000880335A | 1-1 | FM | Bearspaw Rd2 | BEARSPAW ADMIN & TRUCK GARAGE | 20 | 12439 | 201535 | 11842CP000 | NW |  |  | 3432 | 0 | Yes | 3517246 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 700 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 5122 | 90
0000880335A | 1-1 | FM | Bowmont Civic Building | BOWMONT CIVIC BUILDING | 20 | 12439 | 201535 | 11787CP000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3517225 | 437 | 437 |  |  | 0 | 0 | 437 |  |  | 0 | 0 | 437 | 437
0000880335A | 1-1 | Parks | Bowness Pk Comfort Station 1 | BOWNESS PARK COMFORT STATION W - SEASONAL 1 | 20 | 12439 | 201537 | 11835FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880335A | 1-1 | Parks | Bowness Pk Comfort Station 2 | BOWNESS PARK COMFORT STATION W - SEASONAL 2 | 20 | 12439 | 201537 | 11837FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 119.26 | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Parks | Bowness Pk Comfort Stn Yr Rnd | BOWNESS PARK WASHROOM - YEAR ROUND | 20 | 12439 | 201537 | 12169FM000 | NW |  |  | 751 | 0 |  |  | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 250 | 0 | 2414 | 0
0000880335A | 1-1 | Parks | Bowness Pk Depot | BOWNESS PARK DEPOT | 20 | 12439 | 201537 | 12170FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 119.26 | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Parks | Bowness Pk Garage | BOWNESS PARK GARAGE | 20 | 12439 | 201537 | 31114FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880335A | 1-1 | Parks | Bowness Pk Spray Pool Bldg | BOWNESS PARK SPRAY POOL BUILDING | 20 | 12439 | 201537 | 31115FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 195.17 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 195.17 | 0
0000880335A | 1-1 | Parks | Bowness Pk Tea House/Cons./Kitchen | BOWNESS PARK TEA HOUSE | 20 | 12439 | 201537 | 31002FM000 | NW |  |  | 0 | 0 | Yes | 3524065 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 198 | 0 |  |  | 0 | 0 | 0 |  | 3524070 | 250 | 0 | 1688 | 90
0000880335A | 1-1 | Rec | CAM Building | CAPITAL & ASSET MANAGEMENT ADMINISTRATION BUILDING | 20 | 12439 | 201539 | 30009FM000 | NW |  |  | 724 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 383 | 0 | Yes |  | 60 | 60 | 60 |  |  | 0 | 0 | 2757 | 150
0000880335A | 1-1 | Parks | Canmore Park Depot | CANMORE PARK DEPOT | 20 | 12439 | 201537 | 12531FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397552 | 130.11 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 130.11 | 0
0000880335A | 1-1 | Parks | Confederation Pk Depot | CONFEDERATION PARK DEPOT | 20 | 12439 | 201537 | 12524FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3393521 | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880335A | 1-1 | Parks | Crowfoot Depot | CROWFOOT DEPOT | 20 | 12439 | 201537 | 12217FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397538 | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | FM | EMS #15 | EMS #15 | 20 | 12439 | 204065 | 12134CP000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3517657 | 467 | 467 |  |  | 0 | 0 | 467 |  |  | 0 | 0 | 467 | 467
0000880335A | 1-1 | FM | EMS 5 (Geo Post 5) | EMS #5 | 20 | 12439 | 204065 | 12168CP000 | NW |  |  | 812 | 0 | Yes | 3517750 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 321 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2123 | 90
0000880335A | 1-1 | Rec | Father David Bauer (Norma Bush) | FATHER DAVID BAUER ARENA | 20 | 12439 | 201539 | 11779FM000 | NW |  |  | 1614 | 0 | Yes | 3522055 | 45 | 45 | 45 |  |  | 165 | 0 | Yes | 3398228 (RC) 3522091 | 110 | 110 |  |  | 45 | 0 | 110 |  |  | 1126.5 | 0 | Yes | 3522060 | 191 | 191 | 191 | Yes | 3522054 | 250 | 250 | 6691.5 | 596
0000880335A | 1-1 | Rec | Norma Bush (Father David Bauer) | NORMA BUSH ARENA | 20 | 12439 | 201539 | 15149FM000 | NW |  |  | 1614 |  |  |  | 0 | 0 | 0 |  |  | 165 | 0 | Yes |  | 110 | 110 |  |  | 0 | 0 | 110 |  |  | 1126.5 | 0 | Yes | 3522125 | 191 | 191 | 191 |  |  | 0 | 0 | 5336.5 | 301
0000880335A | 1-1 | Rec | Foothills Aquatic | FOOTHILLS AQUATIC CENTRE | 20 | 12439 | 201539 | 12132FM000 | NW |  |  | 767 | 0 | Yes | 3522819 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1006 | 0 | Yes | 3522825 | 160 | 160 | 160 |  |  | 0 | 0 | 4523 | 250
0000880335A | 1-1 | Rec | Foothills Fieldhouse | FOOTHILLS FIELDHOUSE | 20 | 12439 | 201539 | 12125FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 169 | 0 | Yes |  | 47 | 47 | 47 |  |  | 0 | 0 | 686 | 47
0000880335A | 1-1 | Rec | Foothills Little League Building | FOOTHILLS LITTLE LEAGUE | 20 | 12439 | 201539 | 12133FM000 | NW |  |  | 249 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 | Yes |  | 44 | 44 | 44 |  |  | 0 | 0 | 908 | 44
0000880335A | 1-1 | FM | Georgina Thompson | GEORGINA THOMSON BUILDING | 20 | 12439 | 201535 | 12533CP000 | NW |  |  | 636 | 0 | Yes | 3517888 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 492 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2118 | 90
0000880335A | 1-1 | Parks | Haskayne Legacy Park Pavilion | HASKAYNE LEGACY PARK PAVILION | 20 | 12439 | 201537 | 31519FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3478240 | 187 | 187 |  |  | 0 | 0 | 187 |  |  | 0 | 0 | 187 | 187
0000880335A | 1-1 | Parks | Haskayne Legacy Park Svr Bldg | HASKAYNE LEGACY PARK SERVICE BUILDING | 20 | 12439 | 201537 | 31520FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3478270 | 119 | 119 |  |  | 0 | 0 | 119 |  |  | 0 | 0 | 119 | 119
0000880335A | 1-1 | Parks | North Area Office (Confederation Park) | NORTH AREA OFFICE | 20 | 12439 | 201537 | 12530FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397574 | 130.11 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 130.11 | 0
0000880335A | 1-1 | Rec | North Mount Pleasant Art Center | NORTH MOUNT PLEASANT ART CENTRE | 20 | 12439 | 201539 | 12140FM000 | NW |  |  | 978 | 0 | Yes | 3523435 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 509 | 0 | Yes |  | 77 | 77 | 77 |  |  | 0 | 0 | 3324 | 167
0000880335A | 1-1 | Parks | Nose Hill Park Comfort Station | NOSE HILL WASHROOM | 20 | 12439 | 201537 | 15095FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Parks | Old Firehall #6 | OLD FIREHALL #6 | 20 | 12439 | 201537 | 15094FM000 | NW |  |  | 1053 | 0 | Yes | 3523935 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 436 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2479 | 90
0000880335A | 1-1 | Parks | Queen's Park Cemetery Admin | QUEEN'S PARK CEMETERY ADMINISTRATIVE OFFICE | 20 | 12439 | 201537 | 12532FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 157.22 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 157.22 | 0
0000880335A | 1-1 | Parks | Queen's Park Cemetery Svc Bldg | QUEEN'S PARK CEMETERY SERVICE BUILDING | 20 | 12439 | 201537 | 12534FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880335A | 1-1 | Parks | Queen's Park Chapel & Garage | QUEEN'S PARK CHAPEL & GARAGE | 20 | 12439 | 201537 | 12144FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 211 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 211 | 0
0000880335A | 1-1 | Parks | Queen's Park Mausoleum | QUEEN'S PARK MAUSOLEUM | 20 | 12439 | 201537 | 11802FM000 | NW |  |  | 2074 | 0 | Yes | 3524238 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 784 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3848 | 90
0000880335A | 1-1 | Parks | Riley Park Depot | RILEY PARK DEPOT | 20 | 12439 | 201537 | 12508FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880335A | 1-1 | Rec | Shouldice Activity Centre | SHOULDICE ACTIVITY CENTRE | 20 | 12439 | 201539 | 12526FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 178 | 0 | Yes | 3523103 | 28 | 28 | 28 |  |  | 0 | 0 | 486 | 28
0000880335A | 1-1 | Rec | Shouldice Aquatic | SHOULDICE AQUATIC CENTRE | 20 | 12439 | 201539 | 12527FM000 | NW |  |  | 997 | 0 | Yes | 3523126 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 992 | 0 | Yes |  | 190 | 190 | 190 |  |  | 0 | 0 | 5069 | 280
0000880335A | 1-1 | Rec | Shouldice Arena | SHOULDICE ARENA | 20 | 12439 | 201539 | 15158FM000 | NW |  |  | 874 | 0 | Yes | 3522379 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 450 | 0 | Yes | 3522370 | 77 | 77 | 77 |  |  | 0 | 0 | 3161 | 167
0000880335A | 1-1 | Rec | Shouldice Athletic Park Washroom 2 (1) | SHOULDICE ATHLETIC WOMENS WASHROOM | 20 | 12439 | 201539 | 30014FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 171 | 0 | Yes |  | 26 | 26 | 26 |  |  | 0 | 0 | 457 | 26
0000880335A | 1-1 | Rec | Shouldice Athletic Park Washroom 1 (2) | SHOULDICE ATHLETIC PARK MENS WASHROOM | 20 | 12439 | 201539 | 30015FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 171 | 0 | Yes |  | 26 | 26 | 26 |  |  | 0 | 0 | 457 | 26
0000880335A | 1-1 | Rec | Shouldice Athletic Pk Fieldhouse North/South | SHOULDICE ATHLETIC PARK | 20 | 12439 | 201539 | 0031003FM0 | NW |  |  | 1274 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 806 | 0 | Yes |  | 113 | 113 | 113 |  |  | 0 | 0 | 4313 | 203
0000880335A | 1-1 | Rec | Shouldice Hellard Fieldhouse | SHOULDICE ATHLETIC PARK FIELDHOUSE #1 | 20 | 12439 | 201539 | 30012FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 393 | 0 | Yes |  | 78 | 78 | 78 |  | 3481171 | 250 | 0 | 1751 | 78
0000880335A | 1-1 | Rec | Sir Winston Churchill Aquatic | SIR WINSTON CHURCHILL AQUATIC & RECREATION CENTRE | 20 | 12439 | 201539 | 12540FM000 | NW |  |  | 1274 | 0 | Yes | 3523156 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1025 | 0 | Yes | 3523165 | 155 | 155 | 155 |  |  | 0 | 0 | 4994 | 245
0000880335A | 1-1 | FM | Spyhill Gravel Pit Building A | SPYHILL GRAVEL PIT BUILDING A | 20 | 12439 | 201540 | 12236RD000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 164 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 164 | 0
0000880335A | 1-1 | FM | Spyhill Gravel Pit Building B | SPYHILL GRAVEL PIT BUILDING B | 20 | 12439 | 201540 | 12239RD000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 123 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 123 | 0
0000880335A | 1-1 | FM | Spyhill Gravel Pit Building D | SPYHILL GRAVEL PIT BUILDING D | 20 | 12439 | 201540 | 12238RD000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 123 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 123 | 0
0000880335A | 1-1 | FM | Spyhill WMF Building A (B, F1) | SPYHILL WMF BUILDING A | 20 | 12439 | 201540 | 12224WR000 | NW |  |  | 0 | 0 | Yes | 3521425 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 554 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1544 | 90
0000880335A | 1-1 | FM | Spyhill WMF Building B | SPYHILL WMF BUILDING B | 20 | 12439 | 201540 | 12228WR000 | NW |  |  | 3384 | 0 |  |  | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 408 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4782 | 0
0000880335A | 1-1 | FM | Spyhill WMF Building C (Scalehouse) | SPYHILL WMF BUILDING C | 20 | 12439 | 201540 | 19004WR000 | NW |  |  | 445 | 0 | Yes | 3521478 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1668 | 90
0000880335A | 1-1 | FM | Spyhill WMF Building F | SPYHILL WMF BUILDING F | 20 | 12439 | 201540 | 15173WR000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 292 | 0
0000880335A | 1-1 | FM | Spyhill WMF Building F1 | SPYHILL WMF BUILDING F1 | 20 | 12439 | 201540 | 15165WR000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880335A | 1-1 | FM | Spyhill WMF Building L | SPYHILL WMF BUILDING L | 20 | 12439 | 201540 | 19008WR000 | NW |  |  | 649.92 | 0 | Yes | 3521546 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 700 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2339.92 | 90
0000880335A | 1-1 | FM | Spyhill WMF Building P | SPYHILL WMF BUILDING P | 20 | 12439 | 201540 | 12225WR000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880335A | 1-1 | FM | Spyhill WMF Communication Site 1 | SPYHILL WMF COMMUNICATION SITE 1/ SPYHILL WMF RADIO SITE BLDG | 20 | #N/A | #N/A | #N/A | NW |  |  | 679 | 0 | Yes |  | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 45 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1534 | 45
0000880335A | 1-1 | CFD | Station 10 | FIRE STATION #10 | 20 | 12439 | 201536 | 12118FM000 | NW |  |  | 2149 | 0 | Yes | 3524627 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3476154 | 220 | 220 | Yes | 3524631 | 45 | 45 | 265 |  |  | 289 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4283 | 310
0000880335A | 1-1 | CFD | Station 15 | FIRE STATION #15 | 20 | 12439 | 201536 | 12150FM000 | NW |  |  | 1244 | 0 | Yes | 3524704 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 471 | 0 |  |  | 0 | 0 | 0 |  | 3476301 | 250 | 0 | 3205 | 90
0000880335A | 1-1 | CFD | Station 17 | FIRE STATION #17 | 20 | 12439 | 201536 | 11791FM000 | NW |  |  | 955 | 0 | Yes | 3524739 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396785 | 347 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2292 | 90
0000880335A | 1-1 | CFD | Station 18 | FIRE STATION #18 | 20 | 12439 | 201536 | 11848FM000 | NW |  |  | 1124 | 0 | Yes | 3524746 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3437342 | 450 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2564 | 90
0000880335A | 1-1 | CFD | Station 21 | FIRE STATION #21 | 20 | 12439 | 201536 | 12206FM000 | NW |  |  | 1174 | 0 | Yes | 3524793 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396840 | 412 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2576 | 90
0000880335A | 1-1 | CFD | Station 28 | FIRE STATION #28 | 20 | 12439 | 201536 | 11850FM000 | NW |  |  | 966 | 0 | Yes | 3524848 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 462 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2418 | 90
0000880335A | 1-1 | CFD | Station 34 | FIRE STATION #34 | 20 | 12439 | 201536 | 30018FM000 | NW |  |  | 2046 | 0 | Yes | 3524913 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3476714 | 330 | 0 | Yes | 3524916 | 45 | 45 | 45 |  |  | 593 | 0 |  |  | 0 | 0 | 0 |  | 3476712 | 250 | 0 | 5314 | 90
0000880335A | 1-1 | CFD | Station 35 | FIRE STATION #35 | 20 | 12439 | 201536 | 12882FM000 | NW |  |  | 1362 | 0 | Yes | 3524930 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3476796 | 330 | 0 | Yes | 3524935 | 45 | 45 | 45 |  |  | 407 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3944 | 90
0000880335A | 1-1 | CFD | Station 36 | FIRE STATION #36 | 20 | 12439 | 201536 | 11183FM000 | NW |  |  | 487 | 0 | Yes | 3524949 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3524954 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2662 | 375
0000880335A | 1-1 | CFD | Station 40 | FIRE STATION #40 | 20 | 12439 | 201536 | 17561FM000 | NW |  |  | 2031 | 0 | Yes | 3525054 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3525058 | 220 | 220 |  |  | 45 | 0 | 220 |  | 3397109 | 520 | 0 |  |  | 0 | 0 | 0 |  | 3477069 | 250 | 0 | 4896 | 265
0000880335A | 1-1 | CFD | Station 42 | FIRE STATION #42 | 20 | 12439 | 201536 | 30981FM000 | NW |  |  | 2074 | 0 | Yes | 3525111 | 45 | 45 | 45 |  |  | 460 | 0 | Yes | 3525116 | 330 | 330 |  |  | 45 | 0 | 330 |  | 3397167 | 520 | 0 |  |  | 0 | 0 | 0 |  | 3477207 | 500 | 0 | 5899 | 375
0000880335A | 1-1 | CFD | Station 7 | FIRE STATION #7 | 20 | 12439 | 201536 | 30979FM000 | NW |  |  | 1763 | 0 | Yes | 3525234 | 45 | 45 | 45 |  |  | 460 | 0 |  | 3477597 | 330 | 0 | Yes |  | 45 | 45 | 45 |  | 3397314 | 0 | 0 |  |  | 0 | 0 | 0 |  | 3477594 | 250 | 0 | 4568 | 90
0000880335A | 1-1 | Parks | Thornhill Depot | THORNHILL DEPOT | 20 | 12439 | 201537 | 15121FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 124.68 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 124.68 | 0
0000880335A | 1-1 | Rec | Thornhill Murray Copot (Thornhill Aquatic Ctr) | THORNHILL AQUATIC & RECREATION CENTRE | 20 | 12439 | 201539 | 15144FM000 | NW |  |  | 1092 | 0 | Yes | 3523198 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3480504 | 165 | 0 | Yes | 3523219 | 45 | 45 | 45 |  |  | 650.5 | 0 | Yes | 3523204 | 119 | 119 | 119 |  |  | 0 | 0 | 4621.5 | 209
0000880335A | 1-1 | Rec | Thornhill Aquatic Ctr (Thornhill Murray Copot) | MURRAY COPOT ARENA | 20 | 12439 | 201539 | 11191FM000 | NW |  |  | 1092 |  |  |  | 0 | 0 | 0 |  |  | 220 | 0 |  |  | 165 | 0 |  | 3522149 | 0 | 0 | 0 |  |  | 650.5 | 0 | Yes | 3522143 | 119 | 119 | 119 |  |  | 0 | 0 | 3766.5 | 119
0000880335A | 1-1 | FM | Thornhill Tri Services | THORNHILL TRI-SERVICES BUILDING | 20 | 12439 | 201535 | 12202CP000 | NW |  |  | 1611 | 0 | Yes | 3521625 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 933 | 0 |  |  | 0 | 0 | 0 |  |  | 250 | 0 | 4034 | 90
0000880335A | 1-1 | Rec | Riley Park Outdoor Wading Pool | RILEY PARK OUTDOOR WADING POOL | 20 | 12439 | 201539 | 12505FM000 | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3439789 | 307 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 307 | 0
0000880333A | 1-1 | Parks | 52 St East Area Office | 52 ST EAST AREA OFFICE | 20 | 12437 | 201537 | 12076FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397504 | 140.96 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 140.96 | 0
0000880333A | 1-1 | Rec | Acadia Aquatic & Fitness Ctr | ACADIA AQUATIC & FITNESS CENTRE | 20 | 12437 | 201539 | 15152FM000 | SE |  |  | 683 | 0 | Yes | 3522592 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 598 | 0 | Yes | 3522596 | 99 | 99 | 99 |  |  | 0 | 0 | 3360 | 189
0000880333A | 1-1 | FM | Animal Services | ANIMAL SERVICES CENTRE | 20 | 12437 | 201535 | 15109FM000 | SE |  |  | 1844 | 0 | Yes | 3517183 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3393273 3517190 | 220 | 220 |  | 3517209 | 45 | 0 | 220 |  |  | 1324 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 5013 | 265
0000880333A | 1-1 | Parks | Blackfoot Depot | BLACKFOOT DEPOT | 20 | 12437 | 201537 | 11921FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397523 | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Parks | Blackfoot Depot Office Trailer | BLACKFOOT DEPOT OFFICE TRAILER | 20 | 12437 | 201537 | 31123FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397996 | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Rec | Bob Bahan Aquatic Center | BOB BAHAN AQUATIC & FITNESS CENTRE | 20 | 12439 | 201539 | 12068FM000 | SE |  |  | 1373 | 0 |  | 3522625 | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1129 | 0 |  | 3522632 | 265 | 0 | 0 |  |  | 0 | 0 | 6407 | 0
0000880333A | 1-1 | Parks | Burnsland Cemetery Depot | BURNSLAND CEMETERY DEPOT | 20 | 12437 | 201537 | 12017FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Rec | Calgary Soccer Center Annex | CALGARY SOCCER CENTRE | 20 | 12437 | 201539 | 11955FM000 | SE |  |  | 1874 | 0 | Yes |  | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3398621 (RC) 3522494 | 220 | 220 |  | 3522500 | 45 | 0 | 220 |  |  | 1182 | 0 | Yes | 3522449 | 191 | 191 | 191 |  |  | 0 | 0 | 6892 | 456
0000880333A | 1-1 | Rec | Calgary Soccer Centre | CALGARY SOCCER CENTRE | 20 | 12437 | 201539 | 11955FM000 | SE |  |  | 2142 | 0 | Yes | 3522556 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3398649 (RC) 3522558 | 220 | 220 |  | 3522568 | 45 | 0 | 220 |  |  | 752 | 0 | Yes | 3522542 | 162 | 162 | 162 | Yes | 3522581 | 250 | 250 | 6911 | 677
0000880333A | 1-1 | Parks | Carburn Park Depot | CARBURN PARK DEPOT | 20 | 12437 | 201537 | 12287FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397560 | 124.68 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 124.68 | 0
0000880333A | 1-1 | Parks | Corral Depot/Operations Depot | CORRAL OPERATIONS DEPOT | 20 | 12437 | 201537 | 11616FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397544 | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880333A | 1-1 | FM | Dartmouth Pl | DARTMOUTH PLACE | 20 | 12437 | 201535 | 17531CP000 | SE |  |  | 1826 | 0 | Yes | 3517468 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3393546 3517480 | 220 | 220 |  | 3517483 | 45 | 0 | 220 |  |  | 1225 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4786 | 265
0000880333A | 1-1 | FM | East Calgary WMF Building A | EAST CALGARY WMF BUILDING A | 20 | 12437 | 201540 | 11624WR000 | SE |  |  | 3321 | 0 | Yes | 3517505 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 514 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4825 | 90
0000880333A | 1-1 | FM | East Calgary WMF Building B | EAST CALGARY WMF BUILDING B | 20 | 12437 | 201540 | 11629WR000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 408 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 408 | 0
0000880333A | 1-1 | FM | East Calgary WMF Building C1 Scale | EAST CALGARY WMF BUILDING C1 | 20 | 12437 | 201540 | 19012WR000 | SE |  |  | 356 | 0 | Yes | 3517606 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 287 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1633 | 90
0000880333A | 1-1 | FM | East Calgary WMF Building D | EAST CALGARY WMF BUILDING D | 20 | 12437 | 201540 | 19014WR000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880333A | 1-1 | FM | East Calgary WMF Building F1 | EAST CALGARY WMF BUILDING F1 | 20 | 12437 | 201540 | 15162WR000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 321 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 321 | 0
0000880333A | 1-1 | FM | East Calgary WMF Building H | EAST CALGARY WMF BUILDING H | 20 | 12437 | 201540 | 11993WR000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 292 | 0
0000880333A | 1-1 | FM | East Calgary WMF Building S | EAST CALGARY WMF BUILDING S | 20 | 12437 | 201540 | 20015WR000 | SE |  |  | 1942 | 0 | Yes | 3517537 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1749 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4681 | 90
0000880333A | 1-1 | FM | East Calgary WMF Building T | EAST CALGARY WMF BUILDING T | 20 | 12437 | 201540 | 20016WR000 | SE |  |  | 2455 | 0 | Yes | 3517559 | 45 | 45 | 45 |  |  | 440 | 0 | Yes | 3393619 3517574 | 220 | 220 |  | 3517577 | 45 | 0 | 220 |  |  | 350 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4760 | 265
0000880333A | 1-1 | FM | EMS 3 (Geo Post 3) | EMS #3 | 20 | 12437 | 201535 | 11363CP000 | SE |  |  | 1965 | 0 | Yes | 3517708 | 45 | 45 | 45 |  |  | 440 | 0 | Yes | 3393685 3517712 | 220 | 220 |  |  | 45 | 0 | 220 |  |  | 846 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4766 | 265
0000880333A | 1-1 | Rec | Ernie Starr Arena | ERNIE STARR ARENA | 20 | 12439 | 201539 | 12070FM000 | SE |  |  | 809 | 0 |  | 3522167 | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 600 | 0 |  | 3522171 | 118 | 0 | 0 |  |  | 0 | 0 | 3697 | 0
0000880333A | 1-1 | FM | Fairview Mechanical Building | FAIRVIEW MECHANICAL BUILDING | 20 | 12437 | 201546 | 11437FM000 | SE |  |  | 1317 | 0 | Yes | 3517877 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 482 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2789 | 90
0000880333A | 1-1 | CFD | Fire Headquarters | FIRE HEADQUARTERS | 20 | 12437 | 201536 | 30980FM000 | SE |  |  | 2362 | 0 | Yes | 3525308 | 45 | 45 | 45 |  |  | 550 | 0 |  | 3477893 | 330 | 0 | Yes | 3525321 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3477890 | 500 | 0 | 5757 | 90
0000880333A | 1-1 | FM | Fire Station #26 - Mid-Sun Emerg. Resp. Ctr | MID-SUN EMERGENCY RESPONSE CENTRE | 20 | 12437 | 201536 | 11382FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes |  | 250 | 250 | 500 | 250
0000880333A | 1-1 | FM | Forest Lawn CNS | FOREST LAWN BUILDING | 20 | 12437 | 201535 | 11651CP000 | SE |  |  | 1021 | 0 | Yes | 3517821 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 700 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2711 | 90
0000880333A | 1-1 | FM | Forest Lawn Communication Site 2 | FOREST LAWN COMMUNICATION SITE 2 | 20 | 12439 | 201540 | 11733CP000 | SE |  |  | 827 | 0 | Yes | 3517847 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 45 | 0 | 0 |  |  | 217 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1899 | 45
0000880333A | 1-1 | Rec | Forest Lawn Fieldhouse | FOREST LAWN FIELDHOUSE | 20 | 12439 | 201539 | 12072FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 341 | 0 | Yes | 3523569 | 74 | 74 | 74 |  |  | 0 | 0 | 1155 | 74
0000880333A | 1-1 | Rec | Frank McCool Arena | FRANK MCCOOL ARENA | 20 | 12437 | 201539 | 11218FM000 | SE |  |  | 1312 | 0 | Yes | 3522185 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3522213 | 220 | 220 |  | 3522216 | 45 | 0 | 220 |  |  | 1092 | 0 | Yes | 3522188 | 174 | 174 | 174 |  |  | 0 | 0 | 6053 | 439
0000880333A | 1-1 | Rec | Inglewood Aquatic Center | INGLEWOOD AQUATIC CENTRE | 20 | 12437 | 201539 | 11643FM000 | SE |  |  | 562 | 0 | Yes | 3522931 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 510 | 0 | Yes | 3522938 | 109 | 109 | 109 |  |  | 0 | 0 | 3261 | 199
0000880333A | 1-1 | Parks | Inglewood Bird Sct Colonel Walker House | INGLEWOOD BIRD SANCTUARY COLONEL WALKER HOUSE | 20 | 12437 | 201537 | 10519FM000 | SE |  |  | 0 | 0 | Yes | 3524135 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397852 | 202 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1192 | 90
0000880333A | 1-1 | Parks | Inglewood Bird Sct Visitor Svc | INGLEWOOD BIRD SANCTUARY VISITOR SERVICES | 20 | 12437 | 201537 | 15093FM000 | SE |  | 3438140 | 603 | 0 | Yes | 3524149 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3438142 | 328 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1921 | 90
0000880333A | 1-1 | FM | Manchester Center Building C | MANCHESTER BUILDING C | 20 | 12437 | 201535 | 11557CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 233 | 0
0000880333A | 1-1 | FM | Manchester Center Building D | MANCHESTER BUILDING D | 20 | 12437 | 201540 | 15011RD000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 690 | 0 |  | 3435828 | 330 | 0 | Yes | 3518247 | 90 | 90 | 90 |  |  | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2692 | 90
0000880333A | 1-1 | FM | Manchester Center Building E Annex | MANCHESTER BUILDING E ANNEX | 20 | 12437 | 201535 | 11566CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 550 | 0 |  | 3436062 | 440 | 0 | Yes | 3518790 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2590 | 90
0000880333A | 1-1 | FM | Manchester Center Building E North Tower | MANCHESTER BUILDING E NORTH TOWER | 20 | 12437 | 201535 | 15010CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 550 | 0 |  | 3436100 | 330 | 0 | Yes | 3518848 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2260 | 90
0000880333A | 1-1 | FM | Manchester Center Building E South Tower | MANCHESTER BUILDING E SOUTH TOWER | 20 | 12437 | 201535 | 15009CP000 | SE |  |  | 16428 | 0 | Yes | 3518863 | 45 | 45 | 45 |  |  | 550 | 0 |  | 3436112 | 330 | 0 | Yes | 3518872 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 18823 | 90
0000880333A | 1-1 | FM | Manchester Center Building F | MANCHESTER BUILDING F | 20 | 12437 | 201540 | 15012RD000 | SE |  |  | 2152 | 0 | Yes | 3518257 | 90 | 90 | 90 |  |  | 0 | 0 |  | 3435835 | 0 | 0 |  | 3518262 | 0 | 0 | 0 |  |  | 467 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3609 | 90
0000880333A | 1-1 | FM | Manchester Center Building G | MANCHESTER BUILDING G | 20 | 12437 | 201540 | 15013RD000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 233 | 0
0000880333A | 1-1 | FM | Manchester Center Building H | MANCHESTER BUILDING H | 20 | 12437 | 201535 | 15014CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 330 | 0 |  | 3435846 | 220 | 0 | Yes | 3518281 | 90 | 90 | 90 |  |  | 321 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2031 | 90
0000880333A | 1-1 | FM | Manchester Center Building I | MANCHESTER BUILDING I | 20 | 12437 | 201540 | 11562RD000 | SE |  |  | 444 | 0 | Yes |  | 45 | 45 | 45 |  |  | 330 | 0 |  | 3435852 | 220 | 0 | Yes | 3518292 | 45 | 45 | 45 |  |  | 146 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2435 | 90
0000880333A | 1-1 | FM | Manchester Center Building J (Linked with K) | MANCHESTER BUILDING J | 20 | 12437 | 201535 | 11551CP000 | SE |  |  | 1969 | 0 | Yes |  | 45 | 45 | 45 |  |  | 330 | 0 |  | 3435857 | 220 | 0 | Yes | 3518306 | 45 | 45 | 45 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4047 | 90
0000880333A | 1-1 | FM | Manchester Center Building K (Linked with J) | MANCHESTER BUILDING K | 20 | 12437 | 201535 | 15015CP000 | SE |  |  | 1719 | 0 | Yes | 3518323 | 45 | 45 | 45 |  |  | 0 | 0 |  | 3435868 | 0 | 0 |  | 3518328 | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2447 | 45
0000880333A | 1-1 | FM | Manchester Center Building L | MANCHESTER BUILDING L | 20 | 12437 | 201535 | 12018CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 146 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 146 | 0
0000880333A | 1-1 | FM | Manchester Center Building M | MANCHESTER BUILDING M | 20 | 12437 | 201535 | 11559CP000 | SE |  |  | 2357 | 0 | Yes | 3518345 3518348 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3435882 | 220 | 0 | Yes | 3518353 | 45 | 45 | 45 |  |  | 875 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4967 | 90
0000880333A | 1-1 | FM | Manchester Center Building N | MANCHESTER BUILDING N | 20 | 12437 | 201535 | 11554CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 146 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 146 | 0
0000880333A | 1-1 | FM | Manchester Center Building Q | MANCHESTER BUILDING Q | 20 | 12437 | 201535 | 11547CP000 | SE |  |  | 3082 | 0 | Yes | 3518395 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3470668 | 220 | 0 | Yes | 3518415 | 45 | 45 | 45 |  |  | 875 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 5802 | 90
0000880333A | 1-1 | FM | Manchester Center Building R | MANCHESTER BUILDING R | 20 | 12437 | 201535 | 11549CP000 | SE |  |  | 5277 | 0 | Yes | 3518471 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3470877 | 220 | 0 | Yes | 3518562 | 45 | 45 | 45 |  |  | 602 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 7614 | 90
0000880333A | 1-1 | FM | Manchester Center Building S Fleet Services Bldg | MANCHESTER BUILDING S FLEET SERVICES BUILDING | 20 | 12437 | 201535 | 11555CP000 | SE |  |  | 1122 | 0 | Yes | 3518950 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3436149 | 220 | 0 | Yes | 3518951 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2857 | 90
0000880333A | 1-1 | FM | Manchester Center Building S Pipe Layer Shop | MANCHESTER BUILDING S PIPE LAYER SHOP | 20 | 12437 | 201535 | 15004CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880333A | 1-1 | FM | Manchester Center Building U | MANCHESTER BUILDING U | 20 | 12437 | 201535 | 11567CP000 | SE |  |  | 1689 | 0 | Yes | 3518608 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1225 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3904 | 90
0000880333A | 1-1 | FM | Manchester Center Building X | MANCHESTER BUILDING X | 20 | 12437 | 201540 | 15522RD000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880333A | 1-1 | FM | Manchester Center Building Z | MANCHESTER BUILDING Z | 20 | 12437 | 201535 | 11571CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 146 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 146 | 0
0000880333A | 1-1 | FM | Manchester Center Butler Bldg | MANCHESTER BUTLER BUILDING | 20 | 12437 | 201535 | 11556CP000 | SE |  |  | 1775 | 0 | Yes | 3518592 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 117 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2882 | 90
0000880333A | 1-1 | FM | Manchester IT Building | MANCHESTER IT BUILDING | 20 | 12437 | 201535 | 11564CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 117 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 117 | 0
0000880333A | 1-1 | FM | Manchester Logisitics Center (BLDG A) | MANCHESTER BUILDING A | 20 | 12437 | 201535 | 11558CP000 | SE |  |  | 1821 | 0 | Yes | 3518161 | 45 | 45 | 45 |  |  | 440 | 0 |  | 3435790 | 330 | 0 | Yes | 3518167 | 45 | 45 | 45 |  |  | 1983 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 6224 | 90
0000880333A | 1-1 | FM | Manchester Yards Bldg B | MANCHESTER BUILDING B | 20 | 12437 | 201535 | 11565CP000 | SE |  |  | 1712 | 0 | Yes | 3518205 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3435813 | 220 | 0 | Yes | 3518210 | 45 | 45 | 45 |  |  | 398 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3845 | 90
0000880333A | 1-1 | Rec | Maple Ridge Golf Course | MAPLE RIDGE CLUBHOUSE | 20 | 12437 | 201539 | 11404FM000 | SE |  |  | 448 | 0 | Yes | 3523503 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 223 | 0 | Yes | 3523498 | 30 | 30 | 30 |  |  | 250 | 0 | 2491 | 120
0000880333A | 1-1 | CFD | MAT Centre | MULTI-AGENCY TRAINING CENTRE | 20 | 12437 | 201536 | 11596FM000 | SE |  |  | 1611 | 0 | Yes |  | 45 | 45 | 45 |  |  | 440 | 0 |  | 3437794 | 220 | 0 | Yes |  | 45 | 45 | 45 |  |  | 1213 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4779 | 90
0000880333A | 1-1 | Rec | Max Bell (Ken Bracko) | MAX BELL ARENA | 20 | 12439 | 201539 | 12397FM000 | SE |  |  | 2568 | 0 | Yes |  | 45 | 45 | 45 |  |  | 220 | 0 |  |  | 275 | 0 | Yes | 3522319 | 45 | 45 | 45 |  |  | 757.5 | 0 | Yes |  | 62 | 62 | 62 |  |  | 250 | 0 | 6407.5 | 152
0000880333A | 1-1 | Rec | Ken Bracko (Max Bell) | KEN BRACKO ARENA | 20 | 12439 | 201539 | 12071FM000 | SE |  |  | 2568 | 0 | Yes | 3522302 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3438830 | 275 | 0 |  |  | 0 | 0 | 0 |  |  | 757.5 | 0 | Yes | 3522312 | 62 | 62 | 62 |  |  | 0 | 0 | 5547.5 | 107
0000880333A | 1-1 | FM | Mayland Heights | MAYLAND HEIGHTS PARKS RESOURCE MANAGEMENT | 20 | 12439 | 201535 | 11741CP000 | SE | Yes |  | 1822 | 1822 |  | 3519283 | 45 | 0 | 1822 | Yes |  | 220 | 220 |  | 3395015 3519307 | 220 | 0 |  |  | 45 | 0 | 220 | Yes |  | 842 | 842 |  |  | 0 | 0 | 842 |  |  | 0 | 0 | 4399 | 2884
0000880333A | 1-1 | FM | Mayland Heights (Pesticide Bldg) | MAYLAND HEIGHTS INTEGRATED PESTICIDE MANAGEMENT | 20 | 12439 | 201535 | 11752CP000 | SE | Yes |  | 438 | 438 |  | 3519268 | 90 | 0 | 438 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes |  | 263 | 263 |  |  | 0 | 0 | 263 |  |  | 0 | 0 | 1691 | 701
0000880333A | 1-1 | Rec | New Brighton Athletic Park East (West) | NEW BRIGHTON ATHLETIC PARK EAST FIELDHOUSE | 20 | 12437 | 201539 | 30010FM000 | SE |  |  | 273.5 | 0 | Yes | 3523557 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 277 | 0 | Yes | 3523560 | 47.5 | 47.5 | 47.5 |  |  | 0 | 0 | 2063 | 137.5
0000880333A | 1-1 | Rec | New Brighton Athletic Park West (East) | NEW BRIGHTON ATHLETIC PARK WEST FIELDHOUSE | 20 | 12437 | 201539 | 30011FM000 | SE |  |  | 273.5 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 277 | 0 | Yes | 3523549 | 47.5 | 47.5 | 47.5 |  |  | 0 | 0 | 1073 | 47.5
0000880333A | 1-1 | CFD | Old Fire Station #26 (Wellness Centre) | OLD FIRE STATION #26 | 20 | 12437 | 201536 | 11385FM000 | SE |  |  | 511 | 0 | Yes | 3525365 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1501 | 90
0000880333A | 1-1 | Parks | Pine Creek Nursery Depot (Office) | PINE CREEK NURSERY DEPOT | 20 | 12437 | 201537 | 15106FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 113.84 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 113.84 | 0
0000880333A | 1-1 | Parks | Pine Creek Nursery Quonset | PINE CREEK NURSERY QUONSET | 20 | 12437 | 201537 | 15105FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Parks | Prairie Sky Cemetery Depot | PRAIRIE SKY CEMETERY DEPOT | 20 | 12437 | 201537 | 31509FM000 | SE |  |  | 611 | 0 | Yes | 3524198 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 372 | 0 |  |  | 0 | 0 | 0 |  |  | 250 | 0 | 2473 | 90
0000880333A | 1-1 | Parks | Ralph Klein Pk Interpr Ctr | RALPH KLEIN PARK INTERPRETIVE CENTRE | 20 | 12437 | 201537 | 17072FM000 | SE |  |  | 3093 | 0 |  | 3524266 | 45 | 0 | 0 |  |  | 770 | 0 |  | 3479082 | 330 | 0 |  | 3524324 | 45 | 0 | 0 |  |  | 1277 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 6985 | 0
0000880333A | 1-1 | Parks | Ralph Klein Pk Irrigation Bldg | RALPH KLEIN PARK IRRIGATION BUILDING | 20 | 12437 | 201537 | 17535FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Parks | Ralph Klein Pk Mtce Bldg/Comfort Stn | RALPH KLEIN PARK MAINTENANCE BUILDING | 20 | 12437 | 201537 | 17536FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | FM | RD-7 | ROADS DISTRICT 7 ADMIN BUILDING | 20 | 12437 | 201540 | 12381RD000 | SE |  |  | 1311 | 0 | Yes | 3519819 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2534 | 90
0000880333A | 1-1 | Parks | Reader Rock Garden Depot | READER ROCK GARDEN DEPOT | 20 | 12437 | 201537 | 11580FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 113.84 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 113.84 | 0
0000880333A | 1-1 | Parks | Reader Rock Garden Residence/Café | READER ROCK GARDEN RESIDENCE | 20 | 12437 | 201537 | 15098FM000 | SE |  |  | 1423 | 0 | Yes | 3524356 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3479147 | 220 | 0 |  | 3524358 | 45 | 0 | 0 |  | 3438378 | 257 | 0 |  |  | 0 | 0 | 0 |  | 3479163 | 250 | 0 | 4025 | 45
0000880333A | 1-1 | FM | Senior Services | SENIOR SERVICES | 20 | 12437 | 201535 | 11545CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | Yes | 3521333 | 379 | 379 |  |  | 0 | 0 | 379 |  |  | 0 | 0 | 379 | 379
0000880333A | 1-1 | FM | Shepard OWC Building A (NEW A) | SHEPARD OWC BUILDING A | 20 | 12437 | 201540 | 17070WR000 | SE |  |  | 982 | 0 | Yes | 3520086 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 991 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2963 | 90
0000880333A | 1-1 | FM | Shepard OWC Building B (NEW B) | SHEPARD OWC BUILDING B | 20 | 12437 | 201535 | 17532CP000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 583 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 583 | 0
0000880333A | 1-1 | FM | Shepard OWC Building C | SHEPARD OWC BUILDING C | 20 | 12437 | 201540 | 17069WR000 | SE |  |  | 1923 | 0 | Yes | 3520254 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3395601 3520263 | 220 | 220 |  | 3520266 | 45 | 0 | 220 |  |  | 758 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4416 | 265
0000880333A | 1-1 | FM | Shepard OWC Building D | SHEPARD OWC BUILDING D | 20 | 12437 | 201535 | 17521CP000 | SE |  |  | 1887 | 0 | Yes | 3520508 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3395688 3520530 | 220 | 220 |  |  | 45 | 0 | 220 |  |  | 875 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4497 | 265
0000880333A | 1-1 | FM | Shepard OWC Building H | SHEPARD OWC BUILDING H | 20 | 12437 | 201535 | 20019CP000 | SE |  |  | 1120 | 0 | Yes | 3520651 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3395804 3520662 | 220 | 220 |  | 3520589 3520666 | 45 | 0 | 220 |  |  | 816 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3671 | 265
0000880333A | 1-1 | FM | Shepard OWC Building J | SHEPARD OWC BUILDING J | 20 | 12437 | 201540 | 30003WA000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 292 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 292 | 0
0000880333A | 1-1 | FM | Shepard WMF Building F1 (A, B, F1 OLD) | SHEPARD WMF BUILDING F1 | 20 | 12437 | 201535 | 15119CP000 | SE |  |  | 1889 | 0 |  |  | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3054 | 0
0000880333A | 1-1 | FM | Shepard WMF Building I | SHEPARD WMF BUILDING I | 20 | 12437 | 201540 | 19011WR000 | SE |  |  | 496 | 0 | Yes | 3520722 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1661 | 90
0000880333A | 1-1 | FM | Shepard WMF Building L | SHEPARD WMF BUILDING L | 20 | 12437 | 201535 | 11398CP000 | SE |  |  | 698 | 0 | Yes | 3520738 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 554 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2242 | 90
0000880333A | 1-1 | FM | Shepard WMF Building P | SHEPARD WMF BUILDING P | 20 | 12437 | 201540 | 17071WR000 | SE |  |  | 389 | 0 | Yes | 3520749 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1612 | 90
0000880333A | 1-1 | FM | Shepard WMF Building R | SHEPARD WMF BUILDING R | 20 | 12437 | 201540 | 30031WR000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880333A | 1-1 | Parks | South Midnapore Depot | SOUTH MIDNAPORE DEPOT | 20 | 12437 | 201537 | 17066FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880333A | 1-1 | CFD | Station 1 | FIRE STATION #1 | 20 | 12437 | 201536 | 11731FM000 | SE |  |  | 1152 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 462 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2604 | 90
0000880333A | 1-1 | CFD | Station 12 | FIRE STATION #12 | 20 | 12437 | 201536 | 11747FM000 | SE |  |  | 762 | 0 | Yes | 3524673 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396723 | 433 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2185 | 90
0000880333A | 1-1 | CFD | Station 16 & Highfield Admin | FIRE STATION #16 | 20 | 12437 | 201536 | 10087FM000 | SE |  |  | 6197 | 0 | Yes | 3524713 | 45 | 45 | 45 |  |  | 660 | 0 |  | 3476314 3477839 | 550 | 0 | Yes | 3525304 3524716 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3437321 | 250 | 0 | 9862 | 90
0000880333A | 1-1 | CFD | Station 19 | FIRE STATION #19 | 20 | 12437 | 201536 | 11889FM000 | SE |  |  | 1054 | 0 | Yes | 3524762 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396812 | 520 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2564 | 90
0000880333A | 1-1 | CFD | Station 23 | FIRE STATION #23 | 20 | 12437 | 201536 | 12407FM000 | SE |  |  | 1144 | 0 | Yes | 3524807 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396864 | 477 | 0 |  |  | 0 | 0 | 0 |  | 3437394 | 250 | 0 | 3111 | 90
0000880333A | 1-1 | CFD | Station 25 | FIRE STATION #25 | 20 | 12437 | 201536 | 11444FM000 | SE |  |  | 1189 | 0 | Yes | 3524834 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396893 | 491 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2670 | 90
0000880333A | 1-1 | CFD | Station 30 | FIRE STATION #30 | 20 | 12437 | 201536 | 11886FM000 | SE |  |  | 839 | 0 | Yes | 3524869 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3396939 3524873 | 220 | 220 |  | 3524875 | 45 | 0 | 220 |  | 3396929 | 520 | 0 |  |  | 0 | 0 | 0 |  | 3485770 | 275 | 0 | 3754 | 265
0000880333A | 1-1 | CFD | Station 39 | FIRE STATION #39 | 20 | 12437 | 201536 | 17566FM000 | SE |  |  | 2456 | 0 | Yes | 3525002 | 45 | 45 | 45 |  |  | 230 | 0 | Yes | 3397075 3525006 | 220 | 220 |  |  | 45 | 0 | 220 |  | 3397073 | 635 | 0 |  |  | 0 | 0 | 0 |  | 3476991 | 250 | 0 | 5336 | 265
0000880333A | 1-1 | CFD | Station 41 | FIRE STATION #41 | 20 | 12437 | 201536 | 19001FM000 | SE |  |  | 2290 | 0 | Yes | 3525081 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3437603 | 220 | 0 | Yes | 3525086 3525007 | 45 | 45 | 45 |  |  | 462 | 0 |  |  | 0 | 0 | 0 |  | 3477125 | 250 | 0 | 5097 | 90
0000880333A | 1-1 | CFD | Station 43 | TEMPORARY FIRE STATION #43 | 20 | 12437 | 201536 | 31521FM000 | SE |  | 3437849 | 696 | 0 | Yes | 3525377 | 45 | 45 | 45 |  | 3437852 | 330 | 0 |  | 3437854 | 220 | 0 | Yes | 3525378 | 45 | 45 | 45 |  | 3437851 | 264 | 0 |  |  | 0 | 0 | 0 |  | 3437853 | 250 | 0 | 3305 | 90
0000880333A | 1-1 | CFD | Station 9 | FIRE STATION #9 | 20 | 12437 | 201536 | 11439FM000 | SE |  |  | 1256 | 0 | Yes | 3525261 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 427 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2673 | 90
0000880333A | 1-1 | CFD | Training Academy | FIRE TRAINING ACADEMY | 20 | 12437 | 201536 | 12037FM000 | SE |  |  | 888 | 0 | Yes | 3525273 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 809 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2687 | 90
0000880333A | 1-1 | Parks | Union Cemetery Caretakers Ctge | UNION CEMETERY CARETAKERS COTTAGE | 20 | 12437 | 201537 | 10524FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Parks | Union Cemetery Chapel/Mortuary | UNION CEMETERY CHAPEL | 20 | 12437 | 201537 | 12406FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880333A | 1-1 | Parks | Valleyview Spr Park Office | VALLEYVIEW SPRAY PARK OFFICE | 20 | 12437 | 201537 | 11347FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 191 | 0 |  | 3524389 | 0 | 0 | 0 |  |  | 0 | 0 | 191 | 0
0000880333A | 1-1 | CFD | Vehicle Storage | FIRE NEW VEHICLE STORAGE FACILITY | 20 | 12437 | 201536 | 19003FM000 | SE |  |  | 871 | 0 | Yes | 3525336 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 318 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2179 | 90
0000880333A | 1-1 | FM | Water Centre (Manchester) | WATER CENTRE | 20 | 12437 | 201540 | 15143WA000 | SE |  |  | 7982 | 0 | Yes | 3519005 | 45 | 45 | 45 |  |  | 660 | 0 |  | 3471758 | 440 | 0 | Yes | 3519117 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3471922 | 250 | 0 | 11317 | 90
0000880333A | 1-1 | Parks | Corral Carriage House/Corral Depot Trailer | CORRAL CARRIAGE HOUSE | 20 | 12437 | 201537 | 31112FM000 | SE |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397993 | 137 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 137 | 0
0000880332A | 1-1 | Parks | 90 Av Depot | 90 AV DEPOT | 20 | 12437 | 201537 | 12293FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397506 | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880332A | 1-1 | Rec | Beltline Aquatic Center | BELTLINE AQUATIC & FITNESS CENTRE | 20 | 12437 | 201539 | 12428FM000 | SW |  |  | 1184 | 0 | Yes | 3522676 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1206 | 0 | Yes | 3522682 | 191 | 191 | 191 |  |  | 0 | 0 | 5481 | 281
0000880332A | 1-1 | Rec | Canyon Meadows | CANYON MEADOWS AQUATIC & FITNESS CENTRE | 20 | 12437 | 201539 | 15153FM000 | SW |  |  | 1797 | 0 | Yes | 3522790 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3398827 (RC) 3522791 | 220 | 220 |  |  | 45 | 0 | 220 |  |  | 1144 | 0 | Yes | 3522754 | 187 | 187 | 187 |  |  | 0 | 0 | 6733 | 452
0000880332A | 1-1 | Parks | Central Memorial Park Café | CENTRAL MEMORIAL PARK CAFÉ | 20 | 12437 | 201537 | 12886FM000 | SW |  |  | 1892 | 0 | Yes | 3524094 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3478726 | 220 | 0 | Yes | 3524095 | 45 | 45 | 45 |  |  | 639 | 0 |  |  | 0 | 0 | 0 | Yes | 3524097 | 250 | 250 | 4876 | 340
0000880332A | 1-1 | Parks | Central Memorial Park Mtce Bld | CENTRAL MEMORIAL PARK MAINTENANCE BUILDING | 20 | 12437 | 201537 | 12885FM000 | SW |  |  | 966 | 0 | Yes | 3524104 | 45 | 45 | 45 |  |  | 220 | 0 |  | 3478745 | 220 | 0 | Yes | 3524105 | 45 | 45 | 45 |  |  | 187 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2888 | 90
0000880332A | 1-1 | Parks | Centre West Office | RICHMOND CENTRE WEST OFFICE | 20 | 12437 | 201537 | 12005FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880332A | 1-1 | Parks | Chinook Stables Depot | CHINOOK STABLES DEPOT | 20 | 12437 | 201537 | 15107FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397791 | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880332A | 1-1 | Rec | Glenmore Aquatic | GLENMORE AQUATIC CENTRE | 20 | 12437 | 201539 | 11975FM000 | SW |  |  | 704 | 0 | Yes | 3522884 | 90 | 90 | 90 |  |  | 0 | 0 |  | 3398938 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 670 | 0 | Yes |  | 123 | 123 | 123 |  |  | 0 | 0 | 3717 | 213
0000880332A | 1-1 | Rec | Glenmore Boat Patrol | GLENMORE BOAT PATROL | 20 | 12437 | 201539 | 12291FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 150 | 0 | Yes |  | 41 | 41 | 41 |  |  | 0 | 0 | 601 | 41
0000880332A | 1-1 | Rec | Glenmore Sailing School | GLENMORE SAILING SCHOOL | 20 | 12437 | 201539 | 11421FM000 | SW |  |  | 0 | 0 | Yes |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 150 | 0 | Yes |  | 41 | 41 | 41 |  |  | 0 | 0 | 601 | 41
0000880332A | 1-1 | FM | Historic Holy Angels School | HISTORIC HOLY ANGELS SCHOOL | 20 | 12437 | 201535 | 12416CP000 | SW |  |  | 1854 | 0 | Yes | 3517987 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 758 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3602 | 90
0000880332A | 1-1 | Rec | Jimmie Condon Arena (Rose Kohn Arena) | JIMMIE CONDON ARENA | 20 | 12437 | 201539 | 15150FM000 | SW |  |  | 991 | 0 | Yes |  | 45 | 45 | 45 |  |  | 275 | 0 |  |  | 165 | 0 | Yes | 3522292 | 45 | 45 | 45 |  |  | 869 | 0 | Yes | 3522238 | 145 | 145 | 145 |  |  | 0 | 0 | 5080 | 235
0000880332A | 1-1 | Rec | Rose Kohn Arena (Jimmie Condon Arena) | ROSE KOHN ARENA | 20 | 12437 | 201539 | 11949FM000 | SW |  |  | 991 | 0 | Yes | 3522271 | 45 | 45 | 45 |  |  | 275 | 0 |  | 3438771 | 165 | 0 |  |  | 0 | 0 | 0 |  |  | 869 | 0 | Yes | 3522273 | 145 | 145 | 145 |  |  | 0 | 0 | 4720 | 190
0000880332A | 1-1 | Rec | Killarney Aquatic | KILLARNEY AQUATIC & RECREATION CENTRE | 20 | 12437 | 201539 | 12062FM000 | SW |  |  | 2122 | 0 | Yes | 3522989 | 45 | 45 | 45 |  |  | 440 | 0 | Yes | 3399070 (RC) 3523016 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 1066 | 0 | Yes | 3522999 | 187 | 187 | 187 |  |  | 250 | 0 | 8030 | 562
0000880332A | 1-1 | FM | Kingsland Elementary School | KINGSLAND ELEMENTARY SCHOOL | 20 | 12437 | 201546 | 31537FM000 | SW |  |  | 1739 | 0 |  |  | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 492 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3221 | 0
0000880332A | 1-1 | FM | Kohut Building | KOHUT BUILDING | 20 | 12437 | 201540 | 15059LS000 | SW |  |  | 563 | 0 |  |  | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 233 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1786 | 0
0000880332A | 1-1 | Rec | Lakeview Golf Course Clubhouse | LAKEVIEW CLUBHOUSE | 20 | 12437 | 201539 | 12378FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 159 | 0 | Yes |  | 41 | 41 | 41 |  |  | 0 | 0 | 610 | 41
0000880332A | 1-1 | Parks | Mchugh House | MCHUGH HOUSE | 20 | 12437 | 201537 | 30000FM000 | SW |  | 3523989 | 722 | 0 |  | 3523990 | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3523987 | 294 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2006 | 0
0000880332A | 1-1 | Rec | Optimist Arena/Field House (George Blunden) | OPTIMIST ARENA | 20 | 12437 | 201539 | 11595FM000 | SW |  |  | 497 | 0 | Yes | 3522337 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 591 | 0 | Yes |  | 102 | 102 | 102 |  |  | 0 | 0 | 3200 | 192
0000880332A | 1-1 | Rec | George Blunden (Optimist Arena/Field House) | GEORGE BLUNDUN ARENA | 20 | 12437 | 201539 | 15145FM000 | SW |  |  | 497 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 591 | 0 | Yes |  | 102 | 102 | 102 |  |  | 0 | 0 | 2210 | 102
0000880332A | 1-1 | Parks | Prince's Island Pk Depot | PRINCE'S ISLAND PARK DEPOT | 20 | 12437 | 201537 | 12101FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 176 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 176 | 0
0000880332A | 1-1 | Parks | Pump House Depot | PUMP HOUSE DEPOT | 20 | 12437 | 201537 | 15097FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3437969 | 119.26 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 119.26 | 0
0000880332A | 1-1 | FM | RD-9 "Building J" | ROADS DISTRICT 9 BUILDING J | 20 | 12437 | 201540 | 11860RD000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3395356 | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880332A | 1-1 | Parks | Richmond Green Office Trailer/ Crowfoot Depot Trailer | RICHMOND CENTRE WEST OFFICE | 20 | 12437 | 201537 | 12005FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3437916 | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880332A | 1-1 | Parks | Richmond Green Urban Forestry Building | RICHMOND GREEN URBAN FORESTRY BUILDING | 20 | 12437 | 201537 | 15092FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 204 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 204 | 0
0000880332A | 1-1 | Parks | Richmond Green West Depot | RICHMOND GREEN DEPOT | 20 | 12437 | 201537 | 11543FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 129 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 129 | 0
0000880332A | 1-1 | Parks | River Café | RIVER CAFÉ | 20 | 12437 | 201537 | 12103FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397666 | 581 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 581 | 0
0000880332A | 1-1 | FM | Roads District 5 Garage (RD-5) | ROADS DISTRICT 5 GARAGE | 20 | 12437 | 201540 | 11542RD000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 172 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 172 | 0
0000880332A | 1-1 | FM | Roads District 9 Building K | ROADS DISTRICT 9 BUILDING K | 20 | 12437 | 201540 | 11859RD000 | SW | [7 empty] | 0 |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3395360 | 175 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 175 | 0
0000880332A | 1-1 | FM | Sarcee Accessory Storage Building | SARCEE ACCESSORY STORAGE BUILDING | 20 | 12437 | 201535 | 30029CP000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 321 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 321 | 0
0000880332A | 1-1 | FM | Sarcee Administration Building | SARCEE ADMINISTRATION BUILDING | 20 | 12437 | 201535 | 17539CP000 | SW |  |  | 1519 | 0 | Yes |  | 45 | 45 | 45 |  |  | 460 | 0 | Yes | 3395385 3519892 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 1400 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 5224 | 375
0000880332A | 1-1 | FM | Sarcee Vehicle Storage Building | SARCEE VEHICLE STORAGE BUILDING | 20 | 12437 | 201535 | 17540CP000 | SW |  |  | 941 | 0 | Yes | 3520056 | 45 | 45 | 45 |  |  | 460 | 0 | Yes | 3395469 3520060 | 330 | 330 |  |  | 45 | 0 | 330 |  |  | 729 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3975 | 375
0000880332A | 1-1 | FM | Shaganappi Com Site | SHAGANAPPI COMMUNICATION SITE | 20 | 12437 | 201540 | 31132CP000 | SW |  |  | 633 | 0 |  |  | 45 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 45 | 0 | 0 |  |  | 117 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 1605 | 0
0000880332A | 1-1 | FM | Shaganappi Tri Services | SHAGANAPPI TRI-SERVICES BUILDING | 20 | 12437 | 201535 | 11241CP000 | SW |  |  | 1777 | 0 |  | 3521360 | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 1283 | 0 |  |  | 0 | 0 | 0 | Yes | 3521373 | 250 | 250 | 4550 | 250
0000880332A | 1-1 | Parks | Shaw Millennium Park Depot | SHAW MILLENNIUM PARK DEPOT | 20 | 12437 | 201537 | 12479FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3398153 | 291 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 291 | 0
0000880332A | 1-1 | Rec | Southland Leisure Centre | SOUTHLAND LEISURE CENTRE | 20 | 12437 | 201539 | 11919FM000 | SW |  |  | 5147 | 0 | Yes | 3523313 | 45 | 45 | 45 |  |  | 660 | 0 | Yes | 3399372 (RC) 3523338 | 440 | 440 |  |  | 45 | 0 | 440 |  |  | 2045 | 0 | Yes | 3523325 | 276 | 276 | 276 |  |  | 250 | 0 | 13563 | 761
0000880332A | 1-1 | Parks | St Mary'S Cemetery Depot | ST MARY'S CEMETERY DEPOT | 20 | 12437 | 201537 | 12396FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880332A | 1-1 | Parks | Stanley Park Depot | STANLEY PARK DEPOT | 20 | 12437 | 201537 | 12391FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397682 | 130.11 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 130.11 | 0
0000880332A | 1-1 | Parks | Stanley Park Office | STANLEY PARK OFFICE | 20 | 12437 | 201537 | 12390FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397697 | 286 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 286 | 0
0000880332A | 1-1 | CFD | Station 11 | FIRE STATION #11 | 20 | 12437 | 201536 | 19002FM000 | SW |  |  | 2188 | 0 | Yes | 3524638 | 45 | 45 | 45 |  |  | 330 | 0 | Yes | 3524641 | 220 | 220 |  |  | 45 | 0 | 220 |  | 3396676 | 578 | 0 |  |  | 0 | 0 | 0 |  | 3476190 | 250 | 0 | 5111 | 265
0000880332A | 1-1 | CFD | Station 14 | FIRE STATION #14 | 20 | 12437 | 201536 | 15146FM000 | SW |  |  | 1068 | 0 | Yes | 3524687 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3396741 | 376 | 0 |  |  | 0 | 0 | 0 |  | 3476279 | 275 | 0 | 2984 | 90
0000880332A | 1-1 | CFD | Station 2 | FIRE STATION #2 | 20 | 12437 | 201536 | 12080FM000 | SW |  |  | 1162 | 0 | Yes | 3525157 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3397224 | 491 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2643 | 90
0000880332A | 1-1 | CFD | Station 20 | FIRE STATION #20 | 20 | 12437 | 201536 | 11475FM000 | SW |  |  | 1065 | 0 | Yes | 3524776 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 468 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2523 | 90
0000880332A | 1-1 | CFD | Station 24 | FIRE STATION #24 | 20 | 12437 | 201536 | 11361FM000 | SW |  |  | 1311 | 0 | Yes | 3524820 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 482 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2783 | 90
0000880332A | 1-1 | CFD | Station 29 | FIRE STATION #29 | 20 | 12437 | 201536 | 11758FM000 | SW |  |  | 788 | 0 | Yes | 3524855 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 451 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2229 | 90
0000880332A | 1-1 | CFD | Station 33 | FIRE STATION #33 | 20 | 12437 | 201536 | 15174FM000 | SW |  |  | 1933 | 0 | Yes | 3524891 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3437450 | 220 | 0 | Yes | 3524895 | 45 | 45 | 45 |  |  | 578 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 4356 | 90
0000880332A | 1-1 | CFD | Station 37 | FIRE STATION #37 | 20 | 12437 | 201536 | 19000FM000 | SW |  |  | 2231 | 0 | Yes | 3524965 | 45 | 45 | 45 |  |  | 330 | 0 |  | 3437518 | 220 | 0 | Yes | 3524969 | 45 | 45 | 45 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 250 | 0 | 4576 | 90
0000880332A | 1-1 | CFD | Station 5 | FIRE STATION #5 | 20 | 12437 | 201536 | 17565FM000 | SW |  |  | 1206 | 0 | Yes | 3525190 | 45 | 45 | 45 |  |  | 460 | 0 |  | 3477466 | 330 | 0 | Yes | 3525194 | 45 | 45 | 45 |  |  | 635 | 0 |  |  | 0 | 0 | 0 |  | 3477470 | 250 | 0 | 4646 | 90
0000880332A | 1-1 | CFD | Station 6 | FIRE STATION #6 | 20 | 12437 | 201536 | 17050FM000 | SW |  |  | 1521 | 0 | Yes | 3525210 | 45 | 45 | 45 |  |  | 220 | 0 | Yes | 3525214 | 220 | 220 |  |  | 45 | 0 | 220 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 3256 | 265
0000880332A | 1-1 | CFD | Station 8 | FIRE STATION #8 | 20 | 12437 | 201536 | 11658FM000 | SW |  |  | 1398 | 0 | Yes | 3525246 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 410 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 2798 | 90
0000880332A | 1-1 | Rec | Stu Peppard | STU PEPPARD ARENA | 20 | 12437 | 201539 | 11976FM000 | SW |  |  | 1072 | 0 | Yes |  | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 950 | 0 | Yes |  | 146 | 146 | 146 |  |  | 0 | 0 | 4618 | 236
0000880332A | 1-1 | Parks | Tomkins Park Comfort Station | TOMKINS PARK WASHROOM | 20 | 12437 | 201537 | 15108FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 173 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 173 | 0
0000880332A | 1-1 | Rec | Wildflower Art Centre | WILDFLOWER ARTS CENTRE | 20 | 12437 | 201539 | 16494FM000 | SW |  |  | 636 | 0 | Yes | 3523447 | 90 | 90 | 90 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 400 | 0 | Yes |  | 54 | 54 | 54 |  |  | 0 | 0 | 2620 | 144
0000880332A | 1-1 | FM | Eau Claire & Bow River Lumber | EAU CLAIRE & BOW RIVER LUMBER | 20 | 12437 | 201535 | 11753FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  | 3435517 | 187 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 187 | 0
0000880332A | 1-1 | FM | Roads District 6 | ROADS DISTRICT 6 OFFICE/GARAGE | 20 | 12437 | 201540 | 11922RD000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 350 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 350 | 0
0000880332A | 1-1 | Rec | Glenmore Sailing School Classroom | GLENMORE SAILING SCHOOL CLASSROOM BUILDING | 20 | 12437 | 201539 | 31565FM000 | SW |  |  | 0 | 0 |  | 3523703 | 90 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 61 | 0 | 0 |  |  | 0 | 0 | 1661 | 0
0000880332A | 1-1 | FM | Century Gardens North Pavilion | CENTURY GARDENS NORTH PAVILION | 20 | 12437 | 201537 | 31505FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 275 | 0 | Yes | 3523849 | 93 | 93 | 93 |  |  | 0 | 0 | 1298 | 93
0000880332A | 1-1 | FM | Century Gardens South Pavilion | CENTURY GARDENS SOUTH PAVILION | 20 | 12437 | 201537 | 15090FM000 | SW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 200 | 0 | Yes | 3524071 | 85 | 85 | 85 |  |  | 0 | 0 | 1135 | 85
0000880335A | 1-1 | Parks | Confederation Pk Clubhouse | CONFEDERATION PARK CLUBHOUSE | 21 | #N/A | #N/A | #N/A | NW |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 294 | 0 |  |  | 85 | 0 | 0 |  |  | 0 | 0 | 0 | 0
0000880332A | 1-1 | Rec | Babe Ruth Fieldhouse | BABE RUTH FIELDHOUSE |  |  |  |  | SW | [21 empty] | 0 |  |  | 351 | 0 | Yes | 3523635 | 135 | 135 | 135 |  |  | 0 | 0 | 0 | 135
Note on E2: Amanda Kits: copy column k into column e each month for Sejal to keep running tally
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Amount date should be $3,120 - Inv#J014424 - $550 Inv#J014457 - $660 Inv#J014498 - $1,360 Inv#J014619 - $550
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total invoiced amount should be $3,780
Note on J3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total invoice amount should be $28,220 J014425 - $5,114 J014458 - $10,547 J014497 - $8,401 J014620 - $4,158
Note on K3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total invoice amount should be $34,030
Note on J4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total invoiced should be $57,133.73 J014426 - $27,720.95 J014459 - $15,161.78 J014498 - $5,834 J014621 - $8,417
Note on K4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total amount should be $64,269.73
Note on J5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total invoiced should be $68,075.32 J014427 - $28,892.84 J014460 - $18,662.64 J014499 - $11,214.84 J014622 - $11,305.00
Note on K5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total amount should be $81,367.32
Note on J6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total amount to date should be $42,346.37 J014428 - $16,504.26 J014461 - $14,310.11 J014500 - $5,655 J014623 - $5,877
Note on K6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Total amount should be $49,010.37
Note on D210: Amanda Kits: We don't do MEL's for this site
Note on D259: Amanda Kits: Building under construction as per NB Oct 19th. AFA ¦ AEL not complete
Note on D275: Amanda Kits: We do not do MFA's for this site

## PFSS-QQ-01
PFSS-QQ-01 | QUINQUENNIAL PREACTION FIRE SUPPRESSION SYSTEM INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & 13 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | ####COMMON COMPONENTS####
70 | ***Control valves*** (Clause 13.3)
80 | *Waterflow alarm & supervisory signal initiating devices* (Clause 5.2.4 & 5.3.2)
90 | ****Sprinklers**** (Clause 5.2.1)
100 | ***Pipe and fittings*** (Clause 5.2.2)
110 | ***Hanger/braces/supports*** (Clause 5.2.3)
120 | ***Hydraulic design information & information signs*** (Clause 5.2.5, 7, 8, 9)
130 | ***Antifreeze Systems*** (Clause 5.3.3)
140 | ***Alarm Valves*** (Clause 13.4.1.2)
150 | Inspect internally alarm valves and their associated strainers, filters, and
160 | restriction orifices unless tests indicate a greater frequency is necessary
170 | ***Deluge valves*** (Clause 13.4.4)
180 | Inspect internally strainers, filters, restricted orifices, and diaphragm
190 | chambers unless tests indicate a greater frequency is necessary
200 | ***Check Valves*** (Clause 13.4.2)
210 | Valves shall be inspected internally to verify that all of the valve’s
220 | components operate correctly
230 | ***Backflow Prevention Assemblies*** (Clause 13.7)
240 | Inspect internally backflow prevention assemblies to verify that all
250 | components operate correctly, move freely, are in good condition
260 | ####DRY PIPE & PREACTION SYSTEM####
270 | ***Air compressors *** (Clause 13.10.2.1)
280 | ***Gauges***(Clause 13.2.7)
290 | Gauges shall be replaced or tested by comparison with a calibrated gauge
300 | ***Sprinkler pressure-reducing valves*** (Clause 13.5.1.1)
310 | ***Dry Pipe Valves/Quick-Opening Devices*** (Clause 13.4.5)
320 | Inspect internally strainers, filters, and restricted orifices
330 | unless tests indicate a greater frequency is necessary
340 | ***Dry pipe and Preaction valves***(Clause 13.4.3 & 13.4.5)
350 | Inspect internal of valves that can be reset without removal of the faceplate
360 | Inspect internal strainers, filters, restricted orifices and diaphragm chambers
370 | Replace or test gauges every 5 years by comparison with a calibrated gauge
380 | ***Testing*** (Clause 13.4.3)
390 | ***Pressure-Reducing Valves and Relief Valves***
400 | A full flow test shall be conducted on each valve & shall be
410 | compared to previous test results
420 | Review and rectify defects in inspection report by contractor
430 | ***************************************************
440 | Findings Reported To Maintenance Supervisor

## PFSS-TE-01
PFSS-TE-01 | TRIENNIAL PREACTION FIRE SUPPRESSION SYSTEM INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & 13 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | ####COMMON COMPONENTS####
70 | ***Waterflow Alarm Devices*** (5.3.2)
80 | Test the flow switch by opening the inspector’s test connection
90 | ***Control valves*** (Clause 13.3)
100 | ***Deluge valves*** (Clause 13.4.4)
110 | ***Backflow Prevention Assemblies*** (Clause 13.7)
120 | *Waterflow alarm & supervisory signal initiating devices* (Clause 5.2.4 & 5.3.2)
130 | ****Sprinklers**** (Clause 5.2.1)
140 | ***Pipe and fittings*** (Clause 5.2.2)
150 | ***Hanger/braces/supports*** (Clause 5.2.3)
160 | ***Hydraulic design information & information signs*** (Clause 5.2.5, 7, 8, 9)
170 | ***Antifreeze Systems*** (Clause 5.3.3)
180 | ####DRY PIPE & PREACTION SYSTEM####
190 | ***Air compressors *** (Clause 13.10.2.1)
200 | ***Gauges***(Clause 13.2.7)
210 | ***Dry pipe and Preaction valves***(Clause 13.4.3 & 13.4.5)
220 | ***Sprinkler pressure-reducing valves*** (Clause 13.5.1.1)
230 | ***Testing*** (Clause 13.4.3)
240 | Test the preaction systems for air leakage using 1 of the following methods :
250 | (1) Perform a pressure test at 40psi (3.2 bars) for 2 hours. The system shall be
260 | permitted to lose up 3psi (0.2 bar) during the test. Air leak shall be addressed
270 | if the system loses more than 3psi (0.2 bar) during this test
280 | (2) With the system at normal pressure system, shut off the air source
290 | (compressor or shop air) for 4 hours. If the low air pressure goes off within
300 | this period, the air leak shall be addressed
310 | Review and rectify defects in inspection report by contractor
320 | ***************************************************
330 | Findings Reported To Maintenance Supervisor

## PFSS-A-01
PFSS-A-01 | ANNUAL PREACTION FIRE SUPPRESSION SYSTEM INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & 13 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | ####COMMON COMPONENTS####
70 | ***Control valves*** (Clause 13.3)
80 | ***Deluge valves*** (Clause 13.4.4)
90 | ***Backflow Prevention Assemblies*** (Clause 13.7)
100 | *Waterflow alarm & supervisory signal initiating devices* (Clause 5.2.4 & 5.3.2)
110 | ****Sprinklers**** (Clause 5.2.1)
120 | ***Pipe and fittings*** (Clause 5.2.2)
130 | Sprinkler pipe and fittings shall be inspected annually from the floor level
140 | Free of mechanical damage, leakage, and corrosion
150 | ***Hanger/braces/supports*** (Clause 5.2.3)
160 | Sprinkler pipe hangers, braces, and supports shall be inspected
170 | annually from the floor level
180 | Free of damage, leakage and corrosion. Not loose, or unattached
190 | ***Hydraulic design information & information signs*** (Clause 5.2.5, 7, 8, 9)
200 | Verify if signs are provided, securely attached, and legible
210 | ***Antifreeze Systems*** (Clause 5.3.3)
220 | The antifreeze solution shall be tested using the following procedure
230 | ***Backflow Prevention Assemblies*** (Clause 13.7)
240 | Conduct flow test on backflow preventers installed in fire protection piping
250 | at a minimum flow rate of the system demand
260 | ####DRY PIPE & PREACTION SYSTEM####
270 | ***Air compressors *** (Clause 13.10.2.1)
280 | ***Gauges***(Clause 13.2.7)
290 | ***Dry pipe and Preaction valves***(Clause 13.4.3 & 13.4.5)
300 | ***Sprinkler pressure-reducing valves*** (Clause 13.5.1.1)
310 | ***Testing*** (Clause 13.4.3)
320 | Conduct of annual trip test of pre-action valves with detailed parameters
330 | After the annual trip test, return the preaction system to service in accordance
340 | with the manufacturer’s instructions
350 | Inspect the interior of the preaction valve & condition of the detection devices
360 | Operate manual actuation devices
370 | Test low temperature alarms, if installed in valve enclosures,
380 | at the beginning of the heating season
390 | Test automatic air pressure maintenance devices, if provided, during the annual
400 | preaction valve trip test, in accordance with the manufacturer’s instructions
410 | Inspect the interior of dry pipe valve when the trip test is conducted
420 | Review and rectify defects in inspection report by contractor
430 | ***************************************************
440 | Findings Reported To Maintenance Supervisor

## PFSS-Q-01
PFSS-Q-01 | QUARTERLY PREACTION FIRE SUPPRESSION SYSTEM INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & 13 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | ####COMMON COMPONENTS####
70 | ***Deluge valves*** (Clause 13.4.4)
80 | ***Backflow Prevention Assemblies*** (Clause 13.7)
90 | ***Control valves*** (Clause 13.3)
100 | Inspect valves that are electrically supervised
110 | Inspect control valve supervisory alarm devices so verify
120 | they are free of physical damage
130 | *Waterflow alarm & supervisory signal initiating devices* (Clause 5.2.4 & 5.3.2)
140 | Inspect waterflow alarm and supervisory signal initiating devices
150 | to verify that they are free of physical damage
160 | Test mechanical waterflow alarm devices including,
170 | but not limited to, water motor gongs
180 | Test vane-type and pressure switch–type waterflow alarm devices (every 6 months)
190 | ####DRY PIPE & PREACTION SYSTEM####
200 | ***Air compressors *** (Clause 13.10.2.1)
210 | ***Gauges***(Clause 13.2.7)
220 | Inspect gauges where air pressure supervision is connected to location
230 | ***Dry pipe and Preaction valves***(Clause 13.4.3 & 13.4.5)
240 | Valves is free from physical damage
250 | Trim valve(s) in normal open or closed position
260 | Valve seat is not leaking
270 | Electrical components are in service
280 | ***Sprinkler pressure-reducing valves*** (Clause 13.5.1.1)
290 | Inspect all valves shall be to verify that the valves are in the following condi
300 | In the open position. Not leaking
310 | Maintaining downstream pressures in accordance with the design criteria
320 | Handwheels installed and unbroken
330 | ***Testing*** (Clause 13.4.3.2)
340 | Test low air pressure alarms, if provided, as per the manufacturer’s instruction
350 | Test the priming water level in supervised preaction systems for compliance
360 | with manufacturer's instructions
370 | Review and rectify defects in inspection report by contractor
380 | ***************************************************
390 | Findings Reported To Maintenance Supervisor

## PFSS-M-01
PFSS-M-01 | MONTHLY PREACTION FIRE SUPPRESSION SYSTEM INSPECTION (SERVER ROOM)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Maintenance Manual, NFPA 25 Chapter 5 & 13 Standard
30 | requirement for inspection
40 | Below task plan is the minimum requirement to follow. Contractor is responsible
50 | to comply with all updated and applicable codes as required
60 | ####COMMON COMPONENTS####
70 | ***Control valves*** (Clause 13.3)
80 | Inspect valves secured with locks or supervised as per applicable NFPA standards
90 | ***Deluge valves*** (Clause 13.4.4)
100 | Valves is free from physical damage
110 | Trim valve(s) in normal open or closed position
120 | Valve seat is not leaking
130 | Electrical components are in service
140 | ***Backflow Prevention Assemblies*** (Clause 13.7)
150 | Inspect reduced-pressure and detector assemblies to ensure differential-sensing
160 | valve relief port is not continuously discharging
170 | #### DRY PIPE & PREACTION SYSTEM ####
180 | ***Dry pipe and Preaction valves***(Clause 13.4.3 & 13.4.5)
190 | Valves is free from physical damage
200 | Trim valve(s) in normal open or closed position
210 | Valve seat is not leaking
220 | Electrical components are in service
230 | ***Gauges***(Clause 13.2.7)
240 | Compare the air pressure gauge near the compressor to the pressure gauge
250 | above the dry pipe or preaction valve
260 | Gauge is operable and not physically damaged
270 | Gauges monitoring air or nitrogen pressure are being maintained
280 | Gauge in good condition and normal water pressure maintained. Pressure:_____ PSI
290 | ***Air compressors*** (Clause 13.10.2.1)
300 | Air compressor is free of physical damage
310 | Power wiring to the air compressor is intact and free of physical damage
320 | Piping from the air compressor to the fire protection
330 | system is intact and free of physical damage
340 | Air compressor anchoring to the structure or to the system
350 | piping is secure, tight, and free of physical damage
360 | Air compressors requiring oil have the required oil amount in the oil reservoir
370 | Review and rectify defects in inspection report by contractor
380 | ***************************************************
390 | Findings Reported To Maintenance Supervisor

## FSS-A-01
FSS-A-01 | ANNUALLY FIRE SPRINKLER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Code NFPA 25 - 2017 For Annually Inspection
30 | System in service on inspection
40 | Protected areas identified
50 | Hydraulic design information sign attached to rise
60 | ***GAUGE AND CONTROL VALVE***(Clause 13.3.2.2)
70 | ***ALARM VALVES, WATERFLOW DEVICES & SUPERVISORY***(Clause 13.4.1)
80 | ***SPRINKLERS & PIPING***(Clause 5.2-5.4)
90 | **BACKFLOW PREVENTION ASSEMBLIES***(Clause 13.7)
100 | ***FIRE DEPARTMENT CONNECTION***(Clause 13.8)
110 | Check valves, strainers, filters and orifices inspected internally every 5 years
120 | To conduct the main drain test (Clause 13.2.5)
130 | *Dry / Deluge Pipe Valves, & Waterflow Devices* (if applicable) Clause 13.4.4
140 | Test all mechanical waterflow devices (incl. water motor gongs) Clause 5.3.2.1
150 | ***Compressor and Air Dryer***(if applicable)
160 | Compressor oil checked
170 | Compressor oil changed
180 | Compressor cut in pressure (PSI)
180 | Compressor cut out pressure (PSI)
200 | Is the compressor supplying air to refrigerated space?
210 | Supply for pressurized air within refrigerated space?
220 | Freezer/cold storage piping inspected for obstruction enters refrigerated area
230 | Compressir includes air drying components in good condition and functioning
240 | Dry air test kit installed on system?
250 | If YES, dry air test kit is good functioning
260 | Air tanks drained
270 | Replace filter as per manufacturer recommendation
280 | Replace desiccant as per manufacturer recommendation
290 | Review and rectify defects in inspection report by contractor
300 | Findings Reported To Maintenance Supervisor
5 | Pre Job Hazard Assessment Completed?
10 | See Code NFPA - 25 For Inspection
20 | System in service on inspection
30 | Protected areas identified
40 | Hydraulic design information sign attached to rise
50 | ***GAUGE AND CONTROL VALVE***
60 | Guage in good condition and normal water pressure maintained. Pressure:______ PSI
70 | Valves in normal open or close position
80 | Sealed, locked, or supervised
90 | Accessible
100 | Free from external leaks
110 | Provided with applicable identification
120 | All control valves operated through full range and returned to normal position during annual inspection
130 | All control valves lubricated during the inspection
140 | PIV opened during annual inspection until spring or torsion felt and backed off 1/4 turn
150 | ***ALARM VALVES, WATERFLOW DEVICES & SUPERVISORY***
160 | Alarm Valves and system riser check valves to be externally inspected
170 | Gauges indicate normal supply water pressure
180 | Valve(s) free of physical damage
190 | Trim valve(s) in normal open or closed position
200 | Retarding chamber or alarm drains not leaking
210 | Test all mechanical waterflow devices (incl. water motor gongs)
220 | Valves and associated strainers, filters and restriction orifices to be inspected internally every 5 years
230 | Test all vane type and pressure switches
240 | Valve supervisory switches/alarms operated properly
250 | Signals from alarm devices were received at Fire Alarm Control Panel
260 | Signals from alarm devices were received by Central Station
270 | ***SPRINKLERS & PIPING***
280 | Head cabinet has sufficient quantity of spare sprinklers available
290 | Wrench available for each type of sprinkler
300 | Sprinklers in service for 50 years or more have been tested for reliability in past 10 years
310 | Sprinklers with Fast Response elements in service 20 years or more have been tested for reliability in past 10 years
320 | Solder-type, high temp 325°F (163°C) sprinklers in service exposed continuously tested for reliability in past 5 years
330 | Sprinklers in service for 75 years or more have been tested for reliability in past 5 years
340 | Sprinklers subject to harsh environments or corrosive atmospheres tested for reliability in the past 5 years
350 | All sprinklers to be inspected from floor level
360 | Sprinklers appear in good external condition
370 | Sprinklers show no signs of leakage
380 | Sprinklers free of corrosion, foreign material, paint or visible obstruction
390 | Sprinklers installed in the proper orientation
400 | Escutscheons have been installed and are not missing
410 | Minimum clearance is being maintained to storage
420 | In overspray accumulation areas sprinkler heads are protected
430 | If YES, do coverings require replacement (accumulations)
440 | Sprinkler system pipe and fittings inspected from floor level
450 | Piping in good condition and free of mechanical damage, leakage and corrosion
460 | Piping is not subject to external loads
470 | Hangers/Seismic Bracing are not damaged, loose or unattached
480 | Assessment of internal condition of piping performed (every 5 years)
490 | **BACKFLOW PREVENTION ASSEMBLIES*** | 13.7.2
500 | Backflow isolation valves in normal open position
510 | Forward flow test conducted at designed flow rate
520 | Backflow performance test conducted
530 | ***FIRE DEPARTMENT CONNECTION***
540 | Fire Department connections are visible and accessible
550 | Couplings or swivels are not damaged and rotate smoothly
560 | Plugs or caps are in place and undamaged
570 | Gaskets are in place
580 | Identification signs are in place
590 | Check valves not leaking
600 | Automatic drain valve is in place and operating properly
610 | Fire Department connections clapper is in place and operating properly
620 | Interior of the connection is inspected for obstruction
630 | Visible piping supplying the fire department connection is undamaged
640 | Check valves and associated strainers, filters and restriction orifices to be inspected internally every 5 years
650 | To conduct the main drain test
660 | Findings Reported To Facility Supervisor And Facility Operations Coordinator

## Summary
Category | EQUIPMENT DESCRIPTION | Assoication | 2017 (8.5) | Enhanced | PM Cost | Average Labour Unit Rate ($) | Vendor | Alert Issues | Quantity of Buildings involved | Quantity of System involved | SEPTENNIAL | QUINQUENNIAL | QUADRENNIAL / TRIENNIAL | BIENNIAL | ANNUAL | SEMI-ANNUAL | QUARTERLY | MONTHLY | WEEKLY | PM Sch in EAM | Trade | Contractor | Diagram | CODE / REGULATORY BODY | REFERENCE / LINKS | REFERENCE / LINKS (2)
1 | LIFE SAFETY (28)
1.1 | Fire Alarm System | STANDARD by Underwriters Laboratories of Canada | Y |  | Allied LS Cost |  | Allied |  | 255 | 255 | N/A | N/A | N/A | N/A | FA-A-01 | N/A | N/A | FA-M-01 | N/A | Y | COC-Electrical | Y (A only) | Fire Alarm Panel | CAN-ULC-S537: Standard for Verification of Fire Alarm System / CAN-ULC-S536: Inspection and Testing of Fire Alarm Systems / National Fire Code - AB 2019 | CAN ULC S537 Standard for Verification of Fire Alarm Systems | CAN ULC-S536 Monthly Fire Alarm Inspection | Codes:
1.2 | Fire Sprinkler System | National Fire Protection Association |  | Y | Allied LS Cost |  | Allied |  | 78 | 99 | N/A | FSS-QQ-01 | N/A | N/A | FSS-A-01 | N/A | FSS-Q-01 | FSS-M-01 | N/A | Y | COC-Electrical | Y (Q & A) |  | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 5 - Sprinkler System | NFPA 25\Chapter 13 - Common Components and Valves | Alberta Building Code, 2014
1.3 | Pre-Action Fire Sprinkler System | National Fire Protection Association |  | Y | Allied LS Cost |  | Allied |  | 1 | 1 | N/A | PFSS-QQ-01 | PFSS-TE-01 | N/A | PFSS-A-01 | N/A | PFSS-Q-01 | PFSS-M-01 | N/A | Y | COC-Electrical | Y (Q & A) |  | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 5 - Sprinkler System | NFPA 25\Chapter 13 - Common Components and Valves | Alberta Building Code, 2014
1.4 | Fire Standbypipes and Hose System | National Fire Protection Association |  | Y |  |  | Allied |  | 11 | 11 | N/A | N/A | N/A | N/A | FSHS-A-01 | N/A | N/A | N/A | N/A | Y | COC-Electrical |  | Standpipe & Hose System | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 6 - Standpipe and Hose Systems | NFPA 25\Chapter 13 - Common Components and Valves | Alberta Fire Code, 2014
1.5 | Automatic External Defibrillator | Municipal Procedures |  | Y |  |  |  |  | 127 | 164 | N/A | N/A | N/A | N/A | N/A | N/A | AED-01 | N/A | N/A | Y | COC-Maintenance | Y (BA only) |  | AED Management (City of Calgary) | aed20management20guide | AED Review - Support Documents | NFPA-96, Ventilation & Fire Protection of Commercial Cooking Equipment
1.6 | Clean Agent Suppression (Vortex) | National Fire Protection Association |  | Y |  |  |  |  | 1 | 1 | N/A | HFE-QQ-01 | N/A | N/A | HFE-A-01 | HFE-S-01 | N/A | N/A | HFE-W-01 | Y | COC-Electrical | Y (QQ & A only) |  | Maintenance Manual, NFPA 25 Chapter 5 & NFPA 770 Chapter 14 Standard | NFPA 770 -2021 Hybrid System | NFPA 25\Chapter 5 - Sprinkler System | NFPA-2001, Clean Agent Fire Protection Systems
1.7 | CO / NO2 / FREON Gas Detector | National Fire Protection Association |  | Y |  |  |  |  | 103 | 287 | N/A | N/A | N/A | N/A | GAS-A-01 | GAS-S-01 | N/A | N/A | N/A | Y | COC-Mechanical | Y (A only) |  | NFPA 72 National Fire Alarm and Signaling Code, COC internal guidelines | NFPA 72_Chapter 14 Inspection, Testing, and Maintenance | Fire safety equipment (calgary.ca) | CAN-ULC-S533: Standard for Egress Door Securing and Releasing Devices
Honeywell E3Point Gas Detection Manual
1.8 | NH3 Ammonia Detection System | Canadian Standard Association | Y | Y |  |  |  |  | 14 | 16 | N/A | N/A | N/A | N/A | BMS-NH3-A-01 | N/A | N/A | N/A | N/A | Y | COC-Instrument | Y | Ammonia Monitoring System | CSA B52-05 Mechanical Refrigeration Code | csa-b52-13-mechanical-refrigeration-code
[9 empty] | 14 | 16 | N/A | N/A | N/A | N/A | BMS-NH3-A-02 | N/A | N/A | N/A | N/A | Y | COC-Instrument | Y
1.9 | NH3 Personal Detector | Canadian Standard Association |  | Y |  |  |  |  | 14 | 14 | N/A | N/A | N/A | N/A | PLSE-NH3-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | Y |  | CSA B52-05 Mechanical Refrigeration Code | csa-b52-13-mechanical-refrigeration-code
1.10 | Emergency Generator | Canadian Standard Association |  | Y |  |  | Allied |  | 68 | 70 | N/A | N/A | N/A | N/A | EG-A-01 | EG-S-01 | N/A | EG-M-01 | EG-W-01 | Y | COC-Electrical | Y (A only) |  | CSA-C282, Emergency Electric Power Supply for Buildings | CSA 282-15 Emergency Power Supply for Buildings |  | CSA-C22.1, Canadian Electrical Code
1.11 | Emergency Lighting | Canadian Standard Association |  | Y | Allied LS Cost |  |  |  | 270 | 676 | N/A | N/A | N/A | N/A | EL-01 | N/A | N/A | EL-M-04 | N/A | Y | COC-Electrical | N |  | CSA-C22.2 no.141, Emergency Lighting / National Building Code - AB 2019 / National Fire Code - AB 2019 | NFC 2019 AB_6.5.1.6 Inspection of Emergency Lighting |  | CSA-C22.2, Emergency Lighting
1.12 | Fire Extinguishers | National Fire Protection Association | Y |  | FE Cost |  | Sprous |  | 372 | 757 | N/A | N/A | N/A | N/A | FE-A-01 | N/A | N/A | FE-M-01 | N/A | Y | COC-Maintenance | Y (A only) |  | NFPA 10: Standard for Portable Fire Extinguisher | NFPA 10_Chapter 7 Inspection, Maintenance, and Recharging
1.13 | Fire Hydrant | National Fire Protection Association |  | Y | FH Cost |  | Allied |  | 35 | 35 | N/A | N/A | N/A | N/A | FH-A-01 | FH-S-02 | N/A | N/A | N/A | Y | COC-Electrician | N |  | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 7 - Private Fire Service Mains |  | 1. National Fire Protection Association (NFPA) Standards:
1.14 | Fire Pumps | National Fire Protection Association |  | Y |  |  | Allied |  | 4 | 8 | N/A | N/A | N/A | N/A | FI-PU-A-01 | N/A | N/A | FI-PU-M-01 | N/A | Y | COC-Electrician | Y (A only) |  | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NPFA 25\Chapter 8 - Fire Pumps |  | CAN/ULC-S524, Installation of Fire Alarm Systems
1.15 | Kitchen fire suppression (Ventilation Hood) | National Fire Protection Association |  | Y | Allied LS Cost |  | Allied |  | 32 | 32 | N/A | N/A | N/A | N/A | N/A | VHD-S-01 | N/A | N/A | N/A | Y | COC-Electrical | Y |  | NFPA-17, 17A (Standard for Dry & Wet Chemical Extinguishing Systems) & 96 (Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations) | NFPA 96_Chapter 11 Procedures for the Use, Inspection, Testing, and Maintenance of Equipment |  | CAN/ULC-S536, Inspection & Testing of Fire Alarm Systems
1.16 | Emergency Eyewash Station & Showers | American National Standards Institute |  | Y |  |  |  |  | 16 | 16 | N/A | N/A | N/A | N/A | EWSS-A-01 | N/A | N/A | N/A | EWSS-W-01 | Y | COC-Maintenance | Y (A only) |  | ANSI/ISEA Z358.1-2014 for Emergency Eyewash and Shower Equipment | ANSI Guide Z358 Eyewash Station & Shower Inspection
1.17 | Safety Worplace Inspection | Municipal Procedures |  | Y |  |  |  |  | 70 | 70 | N/A | N/A | N/A | N/A | SAFETY-W-A-01 | N/A | SAFETY-W-Q-01 | N/A | N/A | Y | COC-Maintenance | N |  | COC Internal Policy | x0516workplaceinspectionfill
1.18 | Quinennial Fall Protection Roof Anchor Inspection (incl. Catwalk / Trav-safe) | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 7 | 7 | N/A | ANCHOR-R-Q-01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | Occupational Health and Safety Code - Alberta (Part 9) | OHS Code - Part 9 Fall Protection
1.19 | Roof Anchors | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 7 | 7 | N/A | N/A | N/A | N/A | ANCHOR-R-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | Occupational Health and Safety Code - Alberta (Part 9) | OHS Code - Part 9 Fall Protection
1.20 | Building Anchors (Inside the building - RC ONLY) | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 27 | TBC | N/A | N/A | N/A | N/A | BANCH-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | Occupational Health and Safety Code - Alberta (Part 9) | OHS Code - Part 9 Fall Protection
1.21 | Fall Protection Roof Anchors | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 7 | 7 | N/A | N/A | N/A | N/A | ANCHOR-R-A-02 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | Occupational Health and Safety Code - Alberta (Part 9) | OHS Code - Part 9 Fall Protection
1.22 | Fall Protection Personal Equip | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 3 | 3 | N/A | N/A | N/A | N/A | PLSE-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | N |  | Occupational Health and Safety Code - Alberta (Part 5) | OHS Code
1.23 | Smoke Detector (Standalone Type) | National Fire Protection Association |  | Y |  |  |  |  | 3 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | SD-M-01 | N/A | Y | COC-Electrical | N |  | NFPA 72, National Fire Alarm and Signaling Code | Kidde smoke detector manual
1.24 | Emergency Trailer | National Fire Protection Association |  | Y |  |  |  |  | 11 | 11 | N/A | N/A | N/A | N/A | LS-FSHS'!A1 | N/A | N/A | N/A | N/A | Y | COC-Electrical |  |  | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 6 - Standpipe and Hose Systems | NFPA 25\Chapter 13 - Common Components and Valves | Alberta Fire Code, 2014
1.25 | Dock Leveller | American National Standards Institute |  | Y |  |  |  |  | 2 | 2 | N/A | N/A | N/A | N/A | LFT-DLV-A-01 | LFT-DLV-S-01 | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | ANSI MH30.1-2015 -Performance And Testing Requirements For Dock Leveling Devices | ANSI MH30.1-2022 Dock Leveller Inspection
1.26 | Scissor / Man / Boom / Fork Lift Maintenance | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 11 | 11 | N/A | N/A | N/A | N/A | LFT-SICS-A-01 | N/A | N/A | LFT-SCIS-M-01 | N/A | Y | COC-Maintenance | Y |  | OHS & Manufacturer's manual | OHS Code | Genie Scissor Manual
1.27 | Boom Lift Maintenance | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | 3 | 3 | N/A | N/A | N/A | N/A | LFT-BOOM-A-01 | N/A | LFT-BOOM-Q-01 | N/A | N/A | Y | COC-Maintenance | Y |  |  | Genie Z45_Boom_O&M Manual
1.28 | Anti-Entrapment Cover | Alberta Health Services |  | Y |  |  |  |  | 33 | 12 | AEC-ST-01 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Y | COC-Mechanical | Y |  | AHS - Anti-Entrapment Compliance Plan for Public Swimming Pools | frm-21243_Anti-Entrapment Complinace Plan for Public Swimming Pools
2 | Regulated Equipment (9) | [25 empty] | NFPA 71: Installation, Maintenance, and use of Central Station Signaling Systems
2.1 | Lift & Elevator Certification (Passenger / Freight) - For Industrial use | AEDARSA (Alberta Elevating Devices & Amusement Rides Safety Association) & Elevating Devices, Passenger Ropeways and Amusement Rides Permit Regulation AR286/2002 |  | Y |  |  |  |  | 29 | 48 | N/A | N/A | N/A | ELD-B-01 | N/A | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | AEDARSA (Alberta Elevating Devices & Amusement Rides Safety Association) & Elevating Devices, Passenger Ropeways and Amusement Rides Permit Regulation AR286/2002 | Elevating Device Information ed-03-001 | Requirements_for_Elevating_Devices | NFPA 72D: Installation, Maintenance, and use of Proprietary Protective Signaling Systems
2.2 | Lift / Elevator Maintenance |  |  | Y |  |  |  |  | 29 | 48 | N/A | N/A | N/A | N/A | N/A | N/A | ELEV-Q-01 | N/A | N/A | Y | COC-Maintenance | Y |  | Elevating Devices Codes Regulation AR192/2015 & ASME17.1-2007/CSA B44-07 | Elevating Device Codes Regulation AB_2015
Dumbwaiter
| LPPD | [23 empty] | ASME A17.1-2016 & CSA B44-16-safety-code-for-elevators-and-escalators_Section 8.6 Maintenace of Elevator
2.3 | Escalator Certification (AEDARSA) |  |  | Y |  |  |  |  | 1 | 3 | N/A | N/A | N/A | N/A | ELD-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | AEDARSA (Alberta Elevating Devices & Amusement Rides Safety Association) & Elevating Devices, Passenger Ropeways and Amusement Rides Permit Regulation AR286/2002 | Elevating Device Information ed-03-001 | Requirements_for_Elevating_Devices | NFPA 72E: Automatic Fire Detectors
2.4 | Escalator Maintenance |  |  | Y |  |  |  |  | 1 | 3 | N/A | N/A | N/A | N/A | N/A | N/A | ESC-Q-01 | N/A | N/A | Y | COC-Maintenance | Y |  | Elevating Devices Codes Regulation AR192/2015 & ASME17.1-2007/CSA B44-07 | Elevating Device Codes Regulation AB_2015 |  | NFPA 72E: Automatic Fire Detectors
ASME A17.1-2016 & CSA B44-16-safety-code-for-elevators-and-escalators_Section 8.6.8 Maintenace of Escalators
2.5 | Lift & Elevator (Passenger / Freight / Dumbwaiters) - except for industrial use |  |  | Y |  |  |  |  | 12 | 17 | N/A | N/A | N/A | N/A | ELD-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | AEDARSA (Alberta Elevating Devices & Amusement Rides Safety Association) & Elevating Devices, Passenger Ropeways and Amusement Rides Permit Regulation AR286/2002 | Elevating Device Information ed-03-001 | Requirements_for_Elevating_Devices | NFPA 70E: Standard for Electrical Safety in the Workplace
2.6 | Heating Boilers (Hot Water) Inspection | Alberta Boiler Safety Association (ABSA) | Y | [5 empty] | 92 | 244 | N/A | N/A | HB-TE-01 (Triennial) | HB-B-01 | HB-A-01 | N/A | N/A | HB-M-01 | HB-W-01 | Y | COC-Mechanical | Y (A only) |  | ASME Boiler and Pressure Vessel Code Section VI, Recommended Rules for the Care and Operation of Heating Boiler; | ASME BPVC-VI-2015
| Liquid heat to pressure and temp not exceed 1100 kPa & 121 Deg.C / Steam pressure and temp not exceed 103 kPa & 121 Deg.C | [9 empty] | N/A | N/A | N/A | N/A | HB-A-02 | [8 empty] | Alberta Boiler Safety Association (ABSA) | ab-506_inspection_and_servicing_requirements
2.7 | Pressure Vessels (ABSA) |  |  | Y |  |  |  |  | 6 | 9 | N/A | PV-QQ-01 | PV-QR-01 | N/A | N/A | N/A | N/A | N/A | N/A |  | COC-Mechanical | Y |  | ASME Boiler and Pressure Vessel Code Section VI, Recommended Rules for the Care and Operation of Heating Boiler; | ab-506_inspection_and_servicing_requirements
2.8 | Backflow Preventer (Cross Connection Control for Sprinkler, Domestic) | Bylaw Water Utility 40M2006 | Y | [5 empty] | 230 | 693 | N/A | N/A | N/A | N/A | BP-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | Y |  | City of Calgary - Bylaw Water Utility 40M2006, Form E1059 | Water Utility By Law 40M2006 - Water Utility - CCC |  | CAN-ULC-S553: Standard for Installation of Smoke-Alarms
e1059 cross connection control test report
2.9 | IAQ Testing | Occupational Health and Safety Code - Alberta & Government of Alberta |  | Y |  |  |  |  | 6 | 6 | N/A | N/A | N/A | N/A | N/A | AQ-S-01 | N/A | N/A | N/A | Y | COC-Business-OP | Y |  | Occupational Health and Safety Code - Alberta (Part 4) | OHS Code | Owner Guidelines-indoor-air-quality
3 | Plumbing (13) | [25 empty] | CAN-ULC-S552: Standard for Maintenance and Testing of Smoke-Alarms
3.1 | Domestic Hot Water Heater |  | Y |  |  |  | Gateway / B&M / Chisholm |  | 128 | 187 | N/A | N/A | N/A | N/A | DH-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | National Plumbing Code of Canada - 2015 | National Plumbing Code of Canada 2020 |  | CAN-ULC-S575: Commissioning of Life Safety and Fire Protection Systems.
3.2 | Heat Exchanger - domestic water | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 15 | 76 | N/A | N/A | N/A | N/A | PD-HX-A'!A1 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180 |  | CAN-ULC-S567: Door Closers and Electromagnetic Door Holders
3.3 | Pumps - domestic water, fountain, sanitary, sewage, storm, sump, swimming pool, wastewater (facility) | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 18 | 153 | N/A | N/A | N/A | N/A | PD-PU-A'!A1 | N/A | N/A | N/A | N/A | Y | COC-Mechanical |  |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180 |  | The Occupational Health and Safety Act and Regulations (Alberta)
3.4 | Tank - Expansion |  |  | Y |  |  | Gateway / B&M / Chisholm |  | 64 | 179 | N/A | N/A | N/A | N/A | ET-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | ASME Boiler and Pressure Vessel Code Section VIII, Manufacturer's manual (Armstrong) | Resource\Armstrong Expansion Tank
3.5 | Trap - grease disposal | Waste Water Bylaw 14M2012 |  | Y |  |  |  |  | 7 | 8 | N/A | N/A | N/A | N/A | N/A | N/A | GR-TRP-Q-01 | N/A | N/A | Y | COC-Maintennace | N |  | Waste Water Bylaw 14M2012 | City of Calgary monitor_maintain_grease_interceptor
3.6 | Water Softeners |  | Y |  |  |  | Gateway / B&M / Chisholm |  | 26 | 39 | N/A | N/A | N/A | N/A | N/A | N/A | WS-Q-01 | N/A | N/A | Y | COC-Maintennace | N |  | Industry Practice, Manufacturer's manual (Culligan) | Culligan Water Softener
3.7 | Washbay | Municipal Procedures | Y | [5 empty] | 10 | 10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | WB-W-01 | Y | COC-Maintennace | N |  | Internal policy
3.8 | Septic Tank Clean Out | Waste Water Bylaw 14M2012 |  | Y |  |  |  |  | 7 | 7 | N/A | N/A | N/A | N/A | SMP-A-03 | N/A | N/A | N/A | N/A | Y | COC-Maintennace | Y |  | Internal policy
3.9 | Septic Tank Inspection |  |  | Y | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | ST-W-01 | Y | COC-Maintennace | Y |  | Internal policy
3.10 | Hot Water heater Descaling |  |  | Y |  |  |  |  | 1 | 1 | N/A | N/A | N/A | N/A | N/A | DH-02 | N/A | N/A | N/A | Y | COC-Maintennace | Y |  | By South zone (MANBD)
3.11 | Trap and Drain Priming |  | Y | [5 empty] | 28 | 28 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | TRP-M-01 | N/A | Y | COC-Mechanical | N |  | Industry Practice
3.12 | Sump Pit | Waste Water Bylaw 14M2012 | Y | [5 empty] | 17 | 56 | N/A | N/A | N/A | N/A | SMP-A-02 | N/A | SMP-Q-01 | SMP-M-01 | SMP-W-01 | Y | COC-Maintennace | N |  | Industry Practice
3.13 | Sump Pit (Underground Effluent Tank) |  |  | Y | [6 empty] | N/A | N/A | N/A | N/A | SMP-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintennace | N |  | Industry Practice
4 | Mechanical (20)
4.1 | Air Conditioning Unit | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 112 | 328 | N/A | N/A | N/A | N/A | AC-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | Manufacturer's manual and maintenance checklist | Trane hvac-checklist | AC Unit
4.2 | Air Handling Unit | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 34 | 105 | N/A | N/A | N/A | N/A | AHU-A-01 | N/A | AHU-Q-01 | AHU-M-01 | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180 | AHU
4.4 | Air Cooled Chiller | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 9 | 9 | N/A | N/A | N/A | N/A | ACCH-A-01-R21 | ACCH-A-02-R21 | N/A | ACCH-M-01-R21 | N/A | Y | COC-Mechanical |  |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180 | ACCH
4.5 | Water Cooled Chiller & Cooling Tower | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 5 | 13 | N/A | N/A | N/A | N/A | WCCH-A-01-R21 | WCCH-A-02-R21 | N/A | WCCH-M-01-R21 | N/A | Y | COC-Mechanical |  |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.6 | Compressor - air, refrigerant | ASHARE / ABSA | Y |  |  |  | Gateway / B&M / Chisholm |  | 14 | 29 | N/A | N/A | N/A | N/A | CP-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | Manufacturer's manual
4.7 | Ammonia Condenser (Adiabatic) | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 1 | 1 | N/A | N/A | N/A | N/A | NH3-CD-A-01 | NH3-CD-A-02 | N/A | NH3-CD-M-01 | N/A | To be implemented soon | COC-Mechanical |  |  | As per manufacturer manual | ADIABATIC COOLING SYSTEM_RCSCL
4.8 | Exhaust Fan - including specialized exhaust (diesel, kitchen ventilation) | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 163 | 798 | N/A | N/A | N/A | N/A | EF-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.9 | Energy / Heat Recovery Ventilator | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 8 | 8 | N/A | N/A | N/A | N/A | HRU-A-02-R21 | N/A | HRU-Q-01 | N/A | N/A | Y | COC-Mechanical | N |  | Manufacturer's manual | Venmar HRV O&M manual
| Evaporator | ASHARE |  |  |  |  | Gateway / B&M / Chisholm |  |  |  | N/A | N/A | N/A | N/A | [6 empty] | COC-Mechanical
4.10 | Fan Coil Unit | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 18 | 267 | N/A | N/A | N/A | N/A | FCU-A-01 | N/A | FC-Q-01 | N/A | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.11 | Furnace | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 149 | 323 | N/A | N/A | N/A | N/A | N/A | FN-S-01-R21 | N/A | N/A | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.12 | Heater, Infrared | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 88 | 607 | N/A | N/A | N/A | N/A | HI-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | Manufacturer's manual | Robert Gordon Infrared Heater
4.13 | Humidifier | ASHARE |  | Y |  |  | Gateway / B&M / Chisholm |  | 10 | 27 | N/A | N/A | N/A | N/A | HUM-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
| In Slab Heating | ASHARE |  |  |  |  | Gateway / B&M / Chisholm |  |  |  | N/A | N/A | N/A | N/A | [6 empty] | COC-Mechanical |  |  |  | ASHRAE Standard 180.pdf
| Low Loss Header | ASHARE |  |  |  |  | Gateway / B&M / Chisholm |  |  |  | N/A | N/A | N/A | N/A | [6 empty] | COC-Mechanical |  |  |  | ASHRAE Standard 180.pdf
4.14 | Make-up Air Unit | ASHARE | Y |  |  |  | Gateway / B&M / Chisholm |  | 115 | 219 | N/A | N/A | N/A | N/A | N/A | MUA-S-02-R21 | N/A | N/A | N/A | Y | COC-Mechanical | Y |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.15 | Overhead Door | Occupational Health and Safety Code - Alberta | Y |  |  |  | Gateway / B&M / Chisholm |  | 203 | 942 | N/A | N/A | N/A | N/A | OHD-A-01 | N/A | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | OHD Safety Code Part 3(12)(d) and Section 2(1); Manufacturer's manual | Spiral OHD Owners Manual
4.16 | Rooftop Unit |  | Y |  |  |  | Gateway / B&M / Chisholm |  | 69 | 271 | N/A | N/A | N/A | N/A | N/A | RTU-S-01-R21 | N/A | N/A | N/A | Y | COC-Mechanical | Y |  | ASHARE 180 - Standard Practice for Inspection and Maintenance of Commercial Building HVAC Systems | ASHRAE Standard 180
4.17 | Unit Heater - fuel-fired, force flow |  | Y |  |  |  | Gateway / B&M / Chisholm |  | 208 | 909 | N/A | N/A | N/A | N/A | UH-A-01 | N/A | N/A | N/A | N/A | Y | COC-Mechanical | N |  | Manufacturer's manual | Renzor Unit Heater
4.18 | Solar Panel Mounting System |  |  | Y |  |  | Gateway / B&M / Chisholm |  | 1 | 1 | N/A | N/A | N/A | N/A | SP-BR-A-01 | N/A | N/A | N/A | N/A | Y (WHMSC only) | COC-Mechanical | N |  | Solar Photovoltaic (PV) system Guidelines - Alberta Infrastructure | Panel mounting brackets for Whitehorn Only
4.19 | Chemical Water Treatment - HVAC |  |  | Y |  |  | Gateway / B&M / Chisholm |  | 38 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | WTR-CHEM-Q-01 | N/A | WTR-CHEM-BW-01 | Y | COC-Mechanical | N |  | Water Treatment Program Manual - Government of Alberta (June 2014) | Water Treatment Program Manual_Alberta_2014
4.20 | Diesel Fuel Tank Testing | American Society for Testing and Materials |  | Y |  |  | Gateway / B&M / Chisholm |  | 1 | 6 | N/A | N/A | N/A | N/A | EOC-DT-A-01 | N/A | N/A | N/A | N/A | Y (EOC only) | COC-Mechanical | Y |  | ASTM D975, Standard Specification for Diesel Fuel | Diesel Testing_ASTM D975
4.21 | Heat Pump | [5 empty] | Gateway / B&M / Chisholm
5 | Electrical (Current - 6)
CSA Z463-18 Maintenance of Electrical System Maint Practice
5.1 | Variable Frequency Drive | Canadian Standard Association |  | Y |  |  |  |  | 30 | 198 | N/A | N/A | N/A | N/A | VFD-01'!A1 | VFD-S-01 | N/A | N/A | N/A | Y | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.24; Manufacturer's O&M manual
5.2 | Uninterruptable Power Supply | Canadian Standard Association |  | Y |  |  |  |  | 4 | 4 | N/A | N/A | N/A | N/A | UPS-A-01 | N/A | N/A | N/A | N/A | Y | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.23 | CSA Z463-18 Maint of Electrical System Maint Practice Section 8
5.3 | Barrier Arm Gates |  | Y | [5 empty] | 10 | 21 | N/A | N/A | N/A | N/A | N/A | BAG-S-01 | N/A | N/A | N/A | Y | COC-Electrical | Y |  | Manufacturer's operation manual
5.4 | Parking Car Plugs |  | Y | [5 empty] | 67 | 67 | N/A | N/A | N/A | N/A | EL-CPLUG-A'!A1 | N/A | N/A | N/A | N/A | Y (South only) | COC-Electrical | N |  | By South Zone
5.5 | Heat Trace |  |  | Y |  |  |  |  | 13 | 13 | N/A | N/A | N/A | N/A | N/A | HTRACE-S-02 | N/A | N/A | N/A | Y | COC-Electrical | N |  | By South Zone
5.6 | Power Factor Correction Unit |  |  | Y |  |  |  |  | 19 | 19 | N/A | N/A | N/A | N/A | PFCU-A-01 | N/A | N/A | N/A | N/A | Y | COC-Electrical | Y |  | Manufacturer's operation manual | APFCU LOVATO DCRL8 PFC
EL-EQUIP-HV (Over 750V) | Electrical (Future - 27) | [23 empty] | CSA Z463-18 Maint of Electrical System Maint Practice Section 8
EL-EQUIP-PDGPB | Power Distribution Switchgear and panel boards | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-PDGPB-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.1 | Switchgear houses switching devices, control, instrument for various loads
EL-EQUIP-TX-LQ | Power Transformer (Liquid Filled) | Canadian Standard Association |  | Y | [6 empty] | N/A | N/A | N/A | N/A | EL-TX-LQ-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.2.1 | Used for step up / down the voltages in power system, use oil for cooling
EL-EQUIP-TX-DRY | Power Transformer (Dry-type) | Canadian Standard Association |  | Y |  |  |  |  | 25 | 64 | N/A | N/A | N/A | N/A | EL-TX-DRY-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.2.2 | Used for step up / down the voltages in power system
EL-EQUIP-HVCB | High voltage power circuit breaker | Canadian Standard Association |  | Y | [6 empty] | N/A | N/A | N/A | N/A | EL-CB-HV-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.8.5 | Breakers with integral trip unit for overcurrent
EL-EQUIP-LV (30V - 750V) | [20 empty] | COC-Electrical
EL-EQUIP-CA | Power Cables | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-CA-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.5
EL-EQUIP-MEB | Metal-enclosed busways | Canadian Standard Association |  | Y | [6 empty] | N/A | N/A | N/A | N/A | EL-MEB-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.6 | Connections between outdoor and indoor equip
EL-EQUIP-DS | Disconnect Switch & Circuit Switcher | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-DS-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.7 | To isolate a circuit from a power source
EL-EQUIP-MCCB | Circuit Breaker (Insulated & Moulded case) | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-MCCB-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.8.2 | Breakers with integral trip unit for overcurrent
EL-EQUIP-LVCB | Low voltage power circuit breaker | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-CB-LV-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.8.3 | Breakers with integral trip unit for overcurrent
EL-EQUIP-MVCB | Medium voltage power circuit breaker | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-CB-MV-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.8.4 | Breakers with integral trip unit for overcurrent
EL-EQUIP-MD | Protection, Control and Metering devices | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-MD-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.10
EL-EQUIP-TX-CT | Instrument Transformer - CTs | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-TX-CT-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.11.2 | Interface between primary circuit and protection, metering device to permit measurement of power system
EL-EQUIP-TX-VT | Instrument Transformer - VTs | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-TX-VT-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.11.3
EL-EQUIP-MOTOR | Motors | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-MOTOR-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.14
EL-EQUIP-MCC | Motor Control Centers (MCC) | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-MCC-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical |  |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.15
EL-EQUIP-DC | DC Battery System | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-DC-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.18
EL-EQUIP-MVMS | Medium voltage motor starters | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-MVMS-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.16
EL-EQUIP-SA | Surge Arrestor | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-SA-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.19 | Protective devices limit surges by discharging or bypassing surging current
EL-EQUIP-CAP | Capacitors | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-CAP-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.20 | P.F. correction, harmonic filters, surge protection and motor starting
EL-SYS
EL-SYS-GB | Grounding and Bonding Systems | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-GB-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.12 | Electrical safety system and critical to personnel safety
EL-SYS-GFPS | Grounding Fault Protection Systems | Canadian Standard Association |  | Y |  |  |  |  | 596 | 596 | N/A | N/A | N/A | N/A | EL-GFPS-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 8.2.13
EL-SYS-LP | Lightning Protection Systems | Canadian Standard Association/ Canadian Electrical Code |  | Y |  |  |  |  | 3 | 3 | N/A | N/A | N/A | N/A | EL-LP-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | N |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 9.17 | CSA Z463-18 Maint of Electrical System Maint Practice Section 9
Arc Flash
EL-EVS | Electric Vehicle Equipment | Canadian Standard Association |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | EL-EVS-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical |  |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 9.24
EL-PDM
EL-PDM-IR | Infrared Scanning and Thermography (PdM) | ANSI |  | Y |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | EL-PDM-IR'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | Y |  | ANSI/NETA MTS-2019, Standard for Maintenance Testing Specification for Electrical Equipment and Power System | ANSI-NETA-MTS-2011_Thermography Survey
[24 empty] | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 7.5.2 | CSA Z463-18 Maint of Electrical System Maint Practice Section 7
EL-PDM-UI | Ultrasound Inspection (PdM) | Canadian Standard Association |  | Y |  |  |  |  | N/A | N.A | N/A | N/A | N/A | N/A | EL-PDM-UI'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | Y |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 7.5.3
EL-PDM-VA | Vibration Analysis for Rotating Machines (PdM) | Canadian Standard Association |  | Y |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | EL-PDM-VA'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical | Y |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 7.5.7
EL-ELV (Not exceed 30V)
EL-ELV-PA | Public Address System | Canadian Standard Association | [8 empty] | N/A | N/A | N/A | N/A | EL-PA-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical |  |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 9.5 | CSA Z463-18 Maint of Electrical System Maint Practice Section 9
EL-ELV-SSS | Surveillance and Security System (CCTV, Access Control System) | Canadian Standard Association | [8 empty] | N/A | N/A | N/A | N/A | EL-SSS-A'!A1 | N/A | N/A | N/A | N/A | X | COC-Electrical |  |  | CSA Z463-18 Maintenance of Electrical Systems (National Standard of Canada), Section 9.7 | CSA Z463-18 Maint of Electrical System Maint Practice Section 9
FO Feedback
Elect PM Interval
Elect PM Interval (Code)
6 | Architecture & Structure (8)
6.1 | Irrigation Sprinkler System |  |  | Y |  |  |  |  | 45 | 45 | N/A | N/A | N/A | N/A | N/A | IRR-S-01 | N/A | N/A | N/A | Y | COC-Maintenance | Y |  | Industry's practice
6.2 | Shoring Post Inspection | Occupational Health and Safety Code - Alberta |  | Y |  |  |  |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | SHP-S-01 | N/A | N/A | N/A | Y | COC-Contractor | Y |  | Architecht's recommendation
6.3 | Structural Inspection | National Building Code of Canada |  | Y |  |  |  |  | 3 | 3 | N/A | N/A | N/A | N/A | STRU-A-01 | N/A | N/A | N/A | N/A | Y | COC-Contractor | Y
6.4 | Metal Staircase |  | Y | [5 empty] | 1 | 1 | N/A | N/A | N/A | N/A | STAIR-A-01 | N/A | N/A | N/A | N/A | X | COC-Contractor | N |  | Industry's practice
6.5 | Roof Inspection |  |  | Y |  |  |  |  | 52 | 52 | N/A | N/A | N/A | N/A | N/A | ROOF-S-01 | N/A | N/A | N/A | Y | COC-Contractor | Y |  | Industry's practice
6.6 | Shoring | Occupational Health and Safety Code - Alberta
6.7 | Post Tensioned / Precast Structure | National Building Code of Canada
6.8 | Metal / Wooden Poles | Canadian Standard Association
7 | Automation (2)
7.1 | Building Management System |  |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | IA-BMS-A'!A1 | N/A | N/A | N/A | N/A | Y (RC ONLY) | COC-Contractor | Y |  | Manufacturer's Standard (Honeywell / Siemens) | Siemens BMS User Guide
7.2 | Sensor Calibration |  |  | Y |  |  |  |  | TBC | TBC | N/A | N/A | N/A | N/A | IA-BMS-SENSOR-A'!A1 | N/A | N/A | N/A | N/A | Y (RC ONLY) | COC-Contractor | Y |  | Manufacturer's Standard (Honeywell / Siemens) | Honeywell Temp sensor
8 | Tools (2)
8.1 | Scissor Lift Maintenance |  |  | Y |  |  |  |  | 9 | 9 | N/A | N/A | N/A | N/A | LFT-SICS-A-01 | N/A | N/A | LFT-SCIS-M-01 | N/A | Y | COC-Maintenance | Y |  | Manufacturer's manual | Genie Scissor Manual
8.2 | Boom Lift Maintenance (In Progress) |  |  | Y
8.3 | Scaffolding / Ladder | Occupational Health and Safety Code - Alberta
9 | Operations Practice
9.1 | Diving Board / Structural Joints | Municipal Procedures

## FSS-QQ-01
FSS-QQ-01 | QUINQUENNIAL FIRE SPRINKLER INSPECTION
Sequence | Description | Type
10 | Pre Job Hazard Assessment Completed? | Question (Yes/No)
20 | Refer to Code NFPA 25 - 2023 for Quinquennial Inspection | Checklist Item
30 | Complete all steps outlined in the "Annual Inspection" before | Checklist Item
40 | proceeding with the "Quinquennial Inspection" | Checklist Item
50 | System in service on inspection | Checklist Item
60 | Protected areas identified | Checklist Item
70 | Hydraulic design information sign attached to riser (Clauses 5.2.5) | Checklist Item
80 | **SPRINKLERS, PIPING, SUPPORTS, SIGNS INSPECT., TESTING, MAINT.**(Clause 5.2-54) | Checklist Item
90 | Replace sprinklers exposed to harsh environment including corrosive | Checklist Item
100 | atmosphere every 5 years if applicable (5.3.1.1.2) | Checklist Item
110 | **GAUGES** (Clauses 13.2.4) | Checklist Item
120 | Replace or test every 5 years (Clause 13.2.4.2) | Checklist Item
130 | Last date of gauge calibrated or replacement: | Checklist Item
140 | Number of Gauges: | Checklist Item
150 | **ALARM VALVES, CHECK VALVES** (Clause 13.4.1-13.4.2) | Checklist Item
160 | Inspect valves internal, strainers, filters & orifices every 5 yrs (13.4.2.1) | Checklist Item
170 | **PRE-ACTION VALVE INSPECTION** (Clause 13.4.3) - If applicable | Checklist Item
180 | Inspect valves internal, strainers, filters & orifices every 5 yrs (13.4.3.1.3) | Checklist Item
190 | **DELUGE VALVES** (if applicable) (Clause 13.4.4) | Checklist Item
200 | Inspect valves internal, strainers, filters and | Checklist Item
210 | orifices every 5 years (Clause 13.4.4.1.3) | Checklist Item
220 | **DRY PIPE VALVES/QUICK-OPENING DEVICES** (Clause 13.4.5) | Checklist Item
230 | Inspect strainers, filters and orifices every 5 years (13.4.5.1.4) | Checklist Item
240 | **PRESSURE-REDUCING VALVES & RELIEF VALVE** (Clause 13.5.1 - 13.5.6) | Checklist Item
250 | A full flow test on each valve every 5 years | Checklist Item
260 | **BACKFLOW PREVENTION ASSEMBLIES**(Clause 13.7) | Checklist Item
270 | Inspect backflow assemblies internally every 5 years (Clause 13.7.1.3) | Checklist Item
280 | **FIRE DEPARTMENT CONNECTION**(Clause 13.8) | Checklist Item
290 | Hydrostatically tested at 150 psi (10 bar) for 2 hours once every 5 yrs (13.8.5) | Checklist Item
300 | **AUTOMATIC AIR VENT** (Clause 13.11) | Checklist Item
310 | Inspect strainers, filters & screens every 5 yrs for damaged or | Checklist Item
320 | corroded parts (Clause 13.11.1) | Checklist Item
330 | **INTERNAL CONDITION OF PIPING** (Clause 14.2.1) | Checklist Item
340 | Assess internal condition of piping every 5 years | Checklist Item
350 | ************************************************* | Checklist Item
360 | Review and rectify defects in inspection report by contractor | Checklist Item
370 | Above task plan is the minimum requirement to follow | Checklist Item
380 | Contractor is responsible to comply with all update and applicable codes as req. | Checklist Item
390 | Findings Reported To Facility Maintenance Coordinator | Question (Yes/No)

## FSS-Q-01
FSS-Q-01 | QUARTERLY FIRE SPRINKLER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to Code NFPA 25 - 2017 For Quarterly Inspection
30 | Is the Building Occupied
40 | System in service for inspection
50 | Hydraulic design information sign attached to rise
60 | ***GAUGE AND CONTROL VALVE***Clause 13.3.2.2
70 | ***ALARM VALVES, WATERFLOW DEVICES & SUPERVISORY*** Clause 13.4.1 & 5.3.2.1
80 | ***PRESSURE REDUCING VALVES AND RELIEF VALVES*** Clause 13.5.1.1
90 | ***HOSE VALVE INSPECTION***Clause 13.6.1.1
100 | **Backflow Prevention Assemblies*** Clause 13.7
110 | ***FIRE DEPARTMENT CONNECTION***Clause 13.8
120 | ***MAIN DRAIN***Clause 13.2.5.2
130 | *Dry / Deluge Pipe Valves, & Waterflow Devices* (if applicable) Clause 13.4.4
140 | *Pressure Reducing Valve & Relief Valve*(Dry / Deluge Pipe Sys) Clause 13.5.1.1
150 | Review and rectify defects in inspection report by contractor
160 | Findings Reported To Maintenance Supervisor
5 | Pre Job Hazard Assessment Completed?
10 | See Code NFPA - 25 For Inspection
20 | Is the Building Occupied?
30 | System in service for inspection?
40 | Hydraulic design information sign attached to rise
50 | ***GAUGE AND CONTROL VALVE***
60 | Gauge in good condition and normal water pressure maintained. Pressure:______ PSI
70 | Valves in normal open or close position
80 | Sealed, locked, or supervised
90 | Accessible
100 | Free from external leaks
110 | Provided with applicable identification
120 | ***ALARM VALVES, WATERFLOW DEVICES & SUPERVISORY***
130 | Alarm Valves and system riser check valves to be externally inspected
140 | Gauges indicate normal supply water pressure
150 | Valve(s) free of physical damage
160 | Trim valve(s) in normal open or closed position
170 | Retarding chamber or alarm drains not leaking
180 | Test all mechanical waterflow devices (incl. water motor gongs)
190 | ***PRESSURE REDUCING VALVES AND RELIEF VALVES*** | 13.5
200 | Valves in the open position
210 | Not leaking
220 | Maintain downstream pressure with design criteria
230 | Handwheels installed and unbroken
240 | Backflow isolation valves in normal open position
250 | ***HOSE VALVE INSPECTION*** | 13.6
260 | Hose caps are in place and not damaged
270 | Hose threads are not damaged
280 | Valves handles are present and not damaged
290 | Gasket are not damaged or show signs of deterioration
300 | No leaks are present
310 | Valves not obstructed or not capable of normal operation
320 | ***FIRE DEPARTMENT CONNECTION***
330 | Fire Department connections are visible and accessible
340 | Couplings or swivels are not damaged and rotate smoothly
350 | Plugs or caps are in place and undamaged
360 | Gaskets are in place
370 | Identification signs are in place
380 | Check valves not leaking
390 | Automatic drain valve is in place and operating properly
400 | Fire Department connections clapper is in place and operating properly
410 | Interior of the connection is inspected for obstruction
420 | Visible piping supplying the fire department connection is undamaged
430 | ***MAIN DRAIN***
440 | Quarterly test required only where sole water supply through backflow preventer and/or pressure reducing valves
450 | ***PREACTION & DELUDGE VALVES***(IF APPLICABLE)
460 | Valve(s) free of physical damage
470 | Trim valve(s) in normal open or closed position
480 | Valve seat is not leaking
490 | Electrical components are in service
500 | Temperature at valve being maintained at not less than 40°F (4°C)
510 | Low temperature alarm functioning
520 | Test all mechanical waterflow devices (incl. water motor gongs)
530 | Tested priming water level as per manufacturer's instructions
540 | Quick-opening device(s) tested, all operated satisfactorily
550 | Low pressure alarms tested
560 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
Existing tasks in EAM
Sequence | Description
10 | Sprinkler; (Nfpa-25): Inspect Control Valves, Supervisory And Alarm Switches
20 | Sprinkler; (Nfpa-25): Ensure All Supervised Valves Are Open
30 | Sprinkler; (Nfpa-25): Record Pressures On All Gauges
40 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
50 | Pre Job Hazard Assessment Completed?

## EG-Q-01
EG-Q-01 | Quinquennial (every 5 years) Emergency Generator Inspection
10 | Refer To Canadian Standards Association (Csa) For Emer Generator Annual Inspection | Checklist Item | Header Equipment | NO
20 | Csa Standard No. C282-15 -- Emergency Electrical Power Supply For Building | Checklist Item | Header Equipment | NO
30 | Inspect insulation of generator windings and carry out insulation (megger) test | Checklist Item | Header Equipment | NO
40 | ***Engine*** | Checklist Item | Header Equipment | NO
50 | Drain and flush the cooling system. Refill the system with new coolant | Checklist Item | Header Equipment | NO
60 | Clean radiator tubes and cooling fins | Checklist Item | Header Equipment | NO
70 | Replace thermostat | Checklist Item | Header Equipment | NO
80 | Inspect valve clearances and adjust as appropriate | Checklist Item | Header Equipment | NO
90 | Conduct an infrared survey of all electrical connections, contacts, and energized components | Checklist Item | Header Equipment | NO
100 | Correct all defects found during inspections and tests | Checklist Item | Header Equipment | NO
110 | Record all inspections, tests, and correction actions in the log | Checklist Item | Header Equipment | NO
120 | Findings Reported To Maintenance Supervisor | Question (Yes/No) | Header Equipment | NO
130 | Pre Job Hazard Assessment Completed? | Question (Yes/No) | Header Equipment | NO

## MECH-CT-A
MECH-CT-A | ANNUALLY COOLING TOWER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Perform chemical testing of system water.
30 | To collect water sample for Legionella Bacteria and submit all water analysis report
40 | Treat as needed to ensure proper water chemistry. Adjust bleed or blowdown rate as required
50 | Inspect blowdown or drain valve.
60 | Clear all debris to ensure proper operation. Repair or replace if needed
70 | Check chemical injector device. Clean as needed.
80 | Check condensing fan open drive system couplings, bearings, and seals for wear and proper alignment.
90 | Adjust, lubricate, repair, or replace as needed.
100 | Check belt tension and any belt wear. Replace if needed
110 | Check sheaves for evidence of improper alignment. Correct as needed
120 | Check for fouling, corrosion, degradation, or dirt/debris accumulation in sump
130 | Clean the strainer, wet decks, nozzles, and exterior louvers as needed.
140 | Check condition and cleanliness of fill and drift eliminator
150 | Check fills are intact and in place without sagging or gaps in packs
160 | Check control box for dirt, debris, and/or loose terminations. Clean and tighten as needed.
170 | Check fan blades and fan housing. Clean, repair, or replace as needed to ensure proper operation.
180 | Assess field-serviceable bearings. Lubricate if necessary
190 | Check for proper fluid flow and for fluid leaks. Clean, adjust, and repair as needed
200 | Check for proper valves and damper operation. Clean, lubricate, repair, replace, or adjust as needed
210 | Check cooling tower motor(s) and pump(s) for proper operation. Repair or replace as needed to ensure proper operation.
220 | Findings Reported To Maintenance Supervisor

## CT-S-01
CT-S-01 | SEMI-ANNUAL COOLING TOWER WINTERIZATION / START-UP
Sequence | Description
10 | **WINTERIZATION**
20 | Turn off chiller on each control panel, ensure condenser pumps are not running
30 | Turn off swipe pump
40 | Turn off cooling towers main make-up valve and swipe pump make-up valve
50 | Slowly open each cooling tower drain valve
60 | Watch water stream coming out at wash basin/floor drain to prevent from flooding
70 | Open drain valve of each water level well beside cooling towers if applicable
80 | Slowly open drain valve of common header
90 | Drain out each tower make-up branch line
100 | Open swipe pump lid and drain out pump, clean pump chamber and filter basket
110 | Lock-out/tag-out
120 | Set up cooling towers enable @OPER OFF in BMS
130 | **START-UP**
140 | Clean swipe pump chamber and filter basket, close pump lid
150 | Turn off drain valves on each tower make-up branch line
160 | Turn off drain valve of common header
170 | Turn off drain valve of each water level well beside cooling towers, if applicable
180 | Turn off each cooling tower drain valve
190 | Turn on cooling towers main make-up valve and swipe pump make-up valve, if applicable
200 | Make sure condenser pump strainer is clean
210 | Turn on chiller and swipe pump on each control panel
220 | Set up cooling towers enable @NONE ON in BMS

## MECH-CP-Q
MECH-CP-Q | QUARTERLY AIR COMPRESSOR INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Check sight glass or dipstick for oil level, add as required.
20 | Check intake filter & clean as required.
30 | Check safety valves for leakage.
40 | Check valve operation.
50 | Check belt condition & tension, adjust as required.
60 | Check piping & hangers for tightness, adjust as required.
70 | Check PRV for operation.
80 | Drain air receiver tank, if required.
90 | Check automatic unloader operation.
100 | Time the compressor from start to stop and vice versa.
110 | Ensure all guards around moving parts are in place and secured properly
120 | Findings reported to Maintenance Supervisor

## CP-A-01
CP-A-01 | ANNUAL AIR COMPRSSOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Wiring For Condition & Connection Tightness
30 | Check Mag Starter & Holding Contacts
40 | Check Voltage Protection Devices
50 | Check Current Protection Devices
60 | Check & Clean Contacts Of Pressure Switch
70 | Blow Out Motor Windings, If Required
80 | Change Oil Reservoir if applicable
90 | Oil Or Grease Motor Bearings, If Required
100 | Check Valves For Leakage
110 | Check Valve Operation
120 | Clean the intake and exhaust valves with thinner or other suitable solvent.
130 | Check Piping & Hangers For Tightness, Adjust As Required
140 | Check PRV For Proper Operation
150 | Check Air Drier Operation & Tightness & Clean Filters
160 | Check Compressor Pulley Is Secured To Shaft & Properly Aligned With Motor Pulley
170 | Check Motor & Pulley Are Secured To Shaft Check Isolators & Adjust As Necessary
180 | Inspect the safety valve operates freely
190 | Check the condition of belt guard
200 | Check the function of pressure switch, replace as needed
210 | Check the motor overload protector, reset as needed
220 | All Oil Used/Removed Will Be Logged Onto Work Order (Qty & Type)
230 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
Existing Task | CP-01
10 | Check Wiring For Condition & Connection Tightness
20 | Check Mag Starter & Holding Contacts
30 | Check Voltage Protection Devices
40 | Check Current Protection Devices
50 | Check & Clean Contacts Of Pressure Switch
60 | Blow Out Motor Windings, If Required
70 | Change Oil Reservoir***
80 | Oil Or Grease Motor Bearings, If Required
90 | Check Valves For Leakage
100 | Check Valve Operation
110 | Clean Valves
120 | Check Piping & Hangers For Tightness, Adjust As Required
130 | Check Prv For Operation
140 | Check Air Drier Operation & Tightness & Clean Filters
150 | Check Compressor Pulley Is Secured To Shaft & Properly Aligned With Motor Pulley
160 | Check Motor & Pulley Are Secured To Shaft Check Isolators & Adjust As Necessary
170 | All Oil Used/Removed Will Be Logged Onto Work Order (Qty & Type)
180 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
190 | Pre Job Hazard Assessment Completed?

## MECH-CD
MECH-CD | ANNUALLY CONDENSING UNIT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment Completed?
10 | Remove Access Panel And Disconnect Power To Unit.
20 | Vacuum Unit Thoroughly. Clean the coils as needed.
30 | Check Internal Component Fastening Devices And Isolation To Ensure All Secure.
40 | Clean Fan Blades And Coil With Blade/Coil Cleaner, Comb Fins As Required.
50 | Record Amperages Condenser Fan - Amps
60 | Record Amperages Condenser Fan - Volts
70 | Record Amperages Compressor Motor - Amps
80 | Record Amperages Compressor Motor - Volts
90 | Test Crankcase Heater Operation.
100 | Check And Record Refrigerant Discharge/Suction Pressures Discharge Pressure
110 | Check And Record Refrigerant Discharge/Suction Pressures Suction Pressure
120 | Perform Electronic Refrigerant Leak Check. Record Observations
130 | Findings Reported To Maintenance Supervisor

## EL-PDM-IR
EL-PDM-IR | INFRARED SCANNING AND THERMOGRAPHY ELECTRICAL INSPECTION
Sequence | Description
10 | Refer to ANSI / NETA MTS-2019, Standard for Maintenance Testing Specification for Inspection
20 | To conduct the thermography survery for all major electrical system including
30 | Electrical utility substations, transformers and feeder poles
40 | Main electrical incoming services, transformers, capacitor banks, etc.
50 | Main electrical switchboards and disconnects
60 | Main electrical distribution panels and disconnects
70 | Uninterruptable electrical power supplies
80 | Generator controls and transfer switches
90 | Lighting and receptacle electrical panels
100 | Motor Control Centers
110 | Service electrical disconnects for motors
120 | Bus Ducts
130 | Inspect any high resistance connections
140 | Inspect any loose componenets
150 | Inspect any overload condition
160 | ***Visual and Mechanical Inspection***
170 | Inspect physical and mechanical condition
180 | Remove panel cover and view equipment through view ports for transmit signals for measurement
190 | ***Scope of Thermography Survery Report***
200 | Description of area and equipment to be tested
210 | Record the discrepancies
220 | Temperature difference bewtween the area of concern and the reference area
230 | Protable cause of temperature difference
240 | Identify inaccessible and / or unavoidable area and / or equipment
250 | Identify load condition at the time of inspection
260 | Provide photographs and / or thermograms of the deficient area
270 | Provide recommended action of repair with estimated cost
280 | Submission of inspection report in soft and hard copies

## EL-PDM-VA
EL-PDM-VA | ROTATING MACHINE VIBRATION ANALYSIS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 7.5.7 requirement for inspection
30 | To monitor changes in the characteristics of rotating machines such as motor, pumps and generators
40 | Measure for any reasonances, imbalance, misalignment and mechanical bearing failure
50 | Measure for brojen rotor bars
60 | Measure for bowed rotors
70 | Measure for esscentric or loose rotor or stator
80 | Measure for uneven air gap between rotor and stator
90 | Measure for laminatioans
100 | Measure for electrical discharge activity
110 | Provide recommended action of repair with estimated cost
120 | Submission of inspection report in soft and hard copies

## EL-PDM-UI
EL-PDM-UI | ULTRASOUND INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 7.5.3 requirement for inspection
30 | Use ultrasound detectors or collector to detect the high frequency from the equipment
40 | Measure for any partial discharge activity
50 | Measure for arcing and tracking
60 | Measure for background noise
70 | Provide recommended action of repair with estimated cost
80 | Submission of inspection report in soft and hard copies

## CHSA-A-01
CHSA-A-01 | ANNUALLY CHILLER SPECTROSCOPIC OIL ANALYSIS
Sequence | Description
10 | Perform spectroscopic analysis on the chillers compressor oil
20 | Test for moisture, acidity, viscosity, metal wear and ferrous denisty
30 | Submission of analysis report from Lab
40 | Rectify the defects if so required
10 | Perform spectroscopic analysis on the chillers compressor oil
20 | Test including spectrometric analysis to identify wear amount
30 | Quantity of particles (ppm)
40 | Nature of particles, addictive, wear or pollution?
50 | Measure Total Acid Number (TAN)
60 | Measure viscosity
70 | Test for any contamination and moisture presence
80 | Provide accpetable range of each parameter and record deficiencies
90 | Submission of analysis report with recommendation / corrective action

## AC-A-01
AC-A-01 | ANNUALLY AIR CONDITIONING UNIT (SPLIT / STANDALONE) INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check and adjust thermostat
30 | ***Outdoor Unit***
40 | Clean any dirt, leaves and debris outside the main cabinet
50 | Inspect the base pan for blocked drain openings
60 | Remove Access Panel And Disconnect Power To Unit.
70 | Vacuum Unit Thoroughly. Clean the coils as needed.
80 | Check Internal Component Fastening Devices And Isolation To Ensure All Secure.
90 | Clean Fan Blades And Coil With Blade/Coil Cleaner, Comb Fins As Required.
100 | Record Amperages Condenser Fan - Amps
110 | Record Amperages Condenser Fan - Volts
120 | Record Amperages Compressor Motor - Amps
130 | Record Amperages Compressor Motor - Volts
140 | Check And Record Refrigerant Discharge/Suction Pressures Discharge Pressure
150 | Check And Record Refrigerant Discharge/Suction Pressures Suction Pressure
160 | Perform Electronic Refrigerant Leak Check. Record Observations
170 | Check the expansion valve and coil temperature
180 | Lubricate parts as needed
190 | ***Indoor Unit***
200 | Clean or replace air filters
210 | Check and clean the cooling coil
220 | Check for leaks in the ductwork if applicable
230 | Check any unusual odors when the unit starts
240 | Listen for any abnormal noise during operating
250 | Check the function of thermostat
260 | Findings Reported To Maintenance Supervisor
Existing task in EAM (AC-01)
Sequence | Description
10 | Just as a Note: Frequency schedule: S (spring) = May F (fall) = September
20 | S F: Check all unit component fastening devices are secure
30 | S F: Inspect rubber gaskets around access doors
40 | S: Replace belts
50 | S F: Check tension and condition of belts and pulley alignment
60 | S F: Replace all interior filters
70 | S F: Clean exterior metal pre-filter
80 | S F: Lubricate motors and fan bearings
90 | S F: Check blower alignment and bearing operation
100 | S F: Check dampers and linkages for damage and wear
110 | S F: Check operation of all safety controls ( flame, high temp, low temp, air fl
120 | HEATING
130 | Record initial combustion analysis
140 | Record initial combustion analysis: O2 __________%, CO __________ppm, CO2 _____
150 | F: Record final combustion analysis:O2 ________%,CO __________ppm,CO2 _______
160 | F: Circle the applicable flame colour, BLUE or YELLOW
170 | F: Check gas supply pressure
180 | F: Inspect heat exchanger
190 | F: Inspect and clean gas burner plate
200 | F: Inspect and clean ignition system and verify operation
210 | F: Inspect condition of flue pipe (indoor units only) and check for proper draft
220 | AIR CONDITIONING (Complete if applicable)
230 | S: Check refrigerant charge
240 | S: Clean condenser and evaporator coil
250 | F: Inspect condenser and evaporator coil
260 | PM TASK: HVAC100
270 | S F: Comb all damaged fins
280 | S: Perform refrigerant leak check: Confirm type______________________________
290 | S: Inspect refrigerant lines and evidence of oil leaks
300 | S: Check compressor oil level
310 | S: Check refrigerant operating temperature and pressures
320 | S: Check condenser fans and tighten set screws
330 | S F: Inspect and clean all condensate pans and clean condensate drains
340 | ELECTRICAL
350 | F: Check electrical terminations are secure and all fuses are intact
360 | F: Inspect and clean contactors
370 | Measure and record motor amperages: a 10% difference is significant
380 | SUPPLY FAN MOTOR: Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
390 | RETURN FAN MOTOR: Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
400 | EXHAUST FAN MOTOR: Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
410 | DESSICANT WHEEL MTR:Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
420 | COMPRESSOR MOTOR :Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
430 | CONDENSOR FAN MOTOR:Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
440 | EVAPORATOR MOTOR :Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
450 | DRFT INDU/PWER VENT:Add Plate Readings for LOW/HIGH SPEED in AMPS/VOLTS in Notes
460 | DEHUMIDIFIER (Complete if applicable)
470 | F: Inspect and clean dehumidifier’s desiccant wheel
480 | F: Inspect chain and/or belt drive on desiccant wheel motor

## EL-PDGPB-A
EL-EQUIP-PDGPB | ANNUALLY POWER DISTRIBUTION GEAR AND PANEL BOARD INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect the integrity and cleanliness of interior and exterior of switchgear cells
50 | Checking for damaged or loosen parts
60 | Proper grounding and anchors
70 | Check for any sign of heating, electrical discharge and moisture
80 | Inspect auxiliary switchgear equipment such as breaker lifts, carts, hoists, rail assemblies
90 | Note any alarm or fault indicators on control devices, reset as required
100 | Function test all protective schemes and control equipment with switching device to ensure correct position
110 | Check the mechanical and electrical interlocks, exercise all active equipment
120 | Note and replace missing or damaged hardware
130 | Exercise, lubricate and adjust linkages, shutters, and other moving parts on switching devices
140 | Verify all withdrawable components are functioning and grounding are engaged properly
150 | ***Electrical Testing***
160 | Inspect bolted connections
170 | Perform insulation resistance testing on bus work and any normally energized components
180 | Perform tests on instrument transformers as required
190 | Perform test on surge arrestors as required
200 | Findings Reported To Maintenance Supervisor

## EL-DS-A
EL-DS-A | ANNUALLY DISCONNECT SWITCHES AND CIRCUIT SWITCHERS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise periodically disconnects tot ensure smooth operation and alignment
50 | Several manual open-and-close operation at set intervals
60 | Inspect disconnects for cleanliness, anchorage, alignment and proper grounding
70 | Function test and verify all mechanism operated contact assemblies, if equipped
80 | Verify proper operation of all heater circuits
90 | Function test all shunt trip devices, if equipped
100 | Ensure fuse clips and latching mechanisms are securely in place
110 | Function test all door interlocks, test each device to confirm correct position
120 | ***Electrical Testing***
130 | Test disconnector for insulation resistance
140 | Test breaker contacts/poles for contact resistance
150 | Inspect bolt connections
160 | Findings Reported To Maintenance Supervisor

## EL-MCCB-A
EL-MCCB-A | ANNUALLY CIRCUIT BREAKERS - INSULATED CASE AND MOULDED CASE INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise periodically disconnects tot ensure smooth operation and alignment
50 | Several manual open-and-close operation at set intervals
60 | Inspect breakers for cleanliness, anchorage, alignment and proper grounding
70 | Verify cell fit, alignment and racking mechanism operation
80 | Exercise electrically operated circuit breakers by control power systems
90 | Verify integrated protective device is set as per engineereed settings
100 | ***Electrical Testing***
110 | Test breakers for insulation resistance
120 | Test breaker contacts/poles for contact resistance
130 | Inspect bolt connections
140 | Findings Reported To Maintenance Supervisor

## EL-CB-LV-A
EL-CB-LV-A | ANNUALLY LOW VOLTAGE POWER CIRCUIT BREAKERS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise periodically breakers tot ensure smooth operation and alignment
50 | Several manual open-and-close operation at set intervals
60 | Inspect breakers for cleanliness, anchorage, alignment and proper grounding
70 | Verify cell fit, alignment and racking mechanism operation
80 | All mechanism operated contacts and truck operated contact should be functioned and verified, if equipped
90 | Test by secondary injection to verify the operation of integrated protection and trip functions
100 | Verify integrated protective device is set as per engineereed settings
110 | ***Electrical Testing***
120 | Test breakers for insulation resistance
130 | Test breaker contacts/poles for contact resistance
140 | Inspect bolt connections
150 | Findings Reported To Maintenance Supervisor

## EL-TX-CT-A
EL-TX-CT-A | ANNUALLY CURRENT TRANSFORMER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechanical condition of equipment and wiring
50 | Verify CT ratings and accuracy class match engineered drawings
60 | Verify appropriate grounding of secondary circuit
70 | Inspect short device for proper operation and cleanliness
80 | ***Electrical Testing***
90 | Measure secondary circuit burden
100 | Inspect bolted connections
110 | Perform insulation resistance testing on bus work
120 | Verify ratio of instrument transformer using primary or secondary method
130 | Perform polarized test on each transformer
140 | Perform excitation test and de-magnetize transformer
150 | Findings Reported To Maintenance Supervisor

## EL-DC-A
EL-DC-A | ANNUALLY DC BATTERY CHARGER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect the area around battery storage to ensure it is clena and dry
50 | Inspect the DC battery system cabinets, racking, mounts, clearances, ventilation in good condition
60 | Observe and npte any alarm/events
70 | Verify charger settings match design specifications
80 | Verify electrolyte levels and measure specifc gravity of cells
90 | Clean corroded/oxidized terminals and apply an oxide inhabitor to connections
100 | ***Electrical Testing***
110 | Measure the battery system voltage from positive to ground and from negative to ground
120 | Perform internal ohmic test on batteries
130 | Perform load test on battery bank
140 | Measure charger float and equalizing voltage levels
150 | Function charger alarms
160 | Inspect bolted connections
170 | Findings Reported To Maintenance Supervisor

## EL-MVMS-A
EL-MVMC-A | ANNUALLY MEDIUM VOLTAGE MOTOR STARTERS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise starters periodically to ensure smooth operation and alignment
50 | Several manual open-and-close operation at set intervals
60 | Inspect starters for cleanliness, anchorage, alignment and proper grounding
70 | Verify cell fit, alignment and racking mechanism operation
80 | Check all mechanical and electrical interlocks
90 | ***Electrical Testing***
100 | Perform insulation resistance test
110 | Perform contact resistance on all poles of starter
120 | Perform dielectric withstand test
130 | Findings Reported To Maintenance Supervisor

## EL-MCC-A
EL-MCC-A | ANNUALLY MOTOR CONTROL CENTRES INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechancal conditon of equipment and wiring
50 | Inspect anchorage, alignment and grounding
60 | Check electrical and work area clearances
70 | Inspect bus work loose connection, damaged insulators, signs of heating
80 | Clean the interior and exterior equipment enclosures
90 | Ensure rating of equipment and protective device setting match electrical drawings
100 | Exercise, lubricate, adjust linkages and other moving parts
110 | Check the mechanical interlocks, exercise all active components
120 | Note and replace missing or damaged hardware
130 | ***Electrical Testing***
140 | Inspect bolted connections
150 | Perform insulation resistance testing on bus work
160 | Peform test on instrument current transformer
170 | Perform test on surge arrestor as required
180 | Findings Reported To Maintenance Supervisor
190 | Perform Infrared thermography to identify any repair issues or malfunctions occur if applicable

## EL-MEB-A
EL-MEB-A | ANNUALLY MTEAL-ENCLOSED BUSWAYS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect the integrity and cleanliness of busways
50 | Check for damaged or loose piece of parts, proper grounding and anchors
60 | Check signs of heating, electrical tracking, moisture or corrosion
70 | Inspect mechanical support and structure
80 | Ensure weep-hole plugs are free and clear of obstructions
90 | Ensure ventilation opening are clear and clean as needed
100 | Replace missing or damaged hardware
110 | Function check heaters if equipped
120 | ***Electrical Testing***
130 | Perform insulation reistance test on bus work
140 | Perform dielectric withstand test on bus work
150 | Perform bonding check from busway grounds to station grounds
160 | Inspect bolted connections
170 | Findings Reported To Maintenance Supervisor

## EL-MOTOR-A
EL-MOTOR-A | ANNUALLY ELECTRICAL MOTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechanical condition of equipment and wiring
50 | Inspect ventilation system, including filters
60 | Inspect lubrication motor system condition including oil levels
70 | Inspect RTD circuits are rated as per design specifications
80 | Inspect bolted electrical terminations
90 | Inspect any abnormal noise or vibration
100 | ***Electrical Testing***
110 | Performing resistance measurement through bolted connections
120 | Perform insulation resistance test
130 | Perform polarization test on motors over 200 HP
140 | Perform dielectric adsorption test on unit under 200 HP
150 | Perform dc dielectric withstand voltage test on motor rated at 2300 V or greater as per ANAI/IEEE95
160 | Perform phase-to-phase stator resistance test on machine at 2300V or greater
170 | Function space heater circuits for proper operation
180 | Measure the voltage, currects, frequencies and compare with the design
190 | Findings Reported To Maintenance Supervisor

## EL-GFPS-A
EL-GFPS-A | ANNUALLY GROUNDING FAULT PROTECTION SYSTEMS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechanical condition of equipment and wiring
50 | Inspect the physical condition of all cases, covers and accessories
60 | Verify target or LED/LCD operation or reset
70 | Clean the components as per manufacturer's instruction
80 | Verify settings as per engineered settings
90 | Verify appropriate grounding equipment and circuits
100 | Download all events, maintenance data, statistical data prior to perform maintenance test
110 | Check tightness of all connections
120 | Inspect and clean shorting devices
130 | ***Electrical Testing***
140 | Performing metering tests on all analog inputs
150 | Check functional operation via primary and secondary injection
160 | Verify operation of all digital outputs by operating the control device
170 | Verify all communication links are operational
180 | Findings Reported To Maintenance Supervisor

## EL-GB-A
EL-GB-A | ANNUALLY GROUNDING AND BONDING SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect grounding and bonding system for completeness
50 | Note excessive corrosion of conductor and connections
60 | ***Electrical Testing***
70 | Perform earth impedance test
80 | Perform point to point resistance test between main ground and all equipment frame and system neutrals
90 | Findings Reported To Maintenance Supervisor

## LS-SD-A
LS-SD-A | ANNUALLY SMOKE DETECTOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 72 - Chapter 14 requirement for inspection
30 | Inspect and clean detectors
40 | Calibrate Detectors
50 | Carry out functional test as per manufacturer's instruction
60 | Press the test buttons for 5 seconds to test the sound operation and flashing LED light or
70 | Test operation with aerosol tester
80 | Verify location and condition
90 | Verify operation of audible and visual alarms and signal
100 | Inspect lithium batteries for corrosion and tightness of connection (if applicable)
110 | Replace 9V battery for smoke detector (if applicable)
120 | Check the expiry date for smoke detector, replace after 10 years
130 | Check ULC marking for any new detectors
140 | Findings Reported To Maintenance Supervisor
Existing task in EAM (SD-01) - COC Annual Smoke Detector Inspection
Sequence | Description
10 | Check The Keys Within The Lock Boxes To Ensure That They Are Correct
20 | Make Sure Keys Will Allow Emergency Responders Access Into The Facility
30 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
40 | Pre Job Hazard Assessment Completed?

## EL-TX-VT-A
EL-TX-VT-A | ANNUALLY VOLTAGE TRANSFORMER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechanical condition of equipment and wiring
50 | Inspect physical condition of all drawers, cabinets and grounding accessories if equipped
60 | Verify fuse are correctly sized and properly installed
70 | Function drawers and withdrawable mechanisms including discharge grounds and short device
80 | Lubricate moving or sliding surfaces
90 | Verify appropriate grounding of secondary circuit
100 | ***Electrical Testing***
110 | Inspect bolted connections
120 | Perform insulation resistance testing on bus work
130 | Verify ratio of instrument transformer using primary or secondary method
140 | Perform polarized test on each transformer
150 | Findings Reported To Maintenance Supervisor

## EL-MD-A
EL-MD-A | ANNUALLY PROTECTION, CONTROL AND METERING DEVICES INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect physical and mechanical condition of equipment and wiring
50 | Inspect the physical condition of all cases, covers and accessories
60 | Verify target or LED/LCD operation or reset
70 | Inspect electromechanically device to verify clean and proper mechanical operation
80 | Clean the components as per manufacturer's instruction
90 | Verify settings as per engineered settings
100 | Verify appropriate grounding equipment and circuits
110 | Download all events, maintenance data, statistical data prior to perform maintenance test
120 | Check tightness of all connections
130 | Download or document settings and logic from the device
140 | Verify correct data and time are displayed on devices
150 | Check for applicable firmware updates and product recalls
160 | Inspect and clean shorting devices
170 | ***Electrical Testing***
180 | Performing metering tests on all analog inputs
190 | Verify SCADA metering values at remote terminals
200 | Check functional operation of each protection element
210 | Verify operation of all enabled digital inputs
220 | Verify operation of all digital outputs by operating the control device
230 | Verify all communication links are operational
240 | Verify operation of all internal logic function used in protection and control system
250 | Findings Reported To Maintenance Supervisor

## EL-CB-HV-A
EL-CB-HV-A | ANNUALLY HIGH VOLTAGE POWER CIRCUIT BREAKERS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise periodically breakers to ensure smooth operation and alignment
50 | Inspect breakers for cleanliness, anchorage, alignment and proper grounding
60 | Inspect all structure and support
70 | Check integrity of insulating medium using appropriate sample and test method
80 | Check and record all level and pressure gages
90 | Function all applicable trip and alarm features
100 | Verify all mechanism operated contact, if equipped
110 | Exercise electrically operated circuit breakers by their control power systems
120 | Verify mechanism charge, trip-free and anti-pump functions
130 | Perform contact travel analysis
140 | Inspect operation of applicable heater circuits
150 | ***Electrical Testing***
160 | Test breakers for insulation resistance
170 | Perform power factor test as required
180 | Test breakers contact /poles for contact resistance
190 | Perform over potential testing and dielectric testing as required
200 | Inspect bolted connections
210 | Findings Reported To Maintenance Supervisor

## ACCH-A-02-R21
ACCH-A-02-R21 | ANNUAL AIR COOLED CHILLER SHUTDOWN (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | ***Seasonal Shut-down***(Fall)
30 | Review control panel for proper operation and recorded fault histories
40 | Check refrigerant levels
50 | Record and log all operating parameters
60 | Shut down chiller and associated chilled and condensing water valves
70 | Conduct refrigerant leak check
80 | Tag chiller out of service
90 | Disable chiller function in BMS (if applicable)
100 | Findings reported to Maintenance Supervisor

## ACCH-A-01-R21
ACCH-A-01-R21 | ANNUAL AIR COOLED CHILLER START UP INSPECTION & CLEANING (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | ***Seasonal Start-up*** (Spring)
30 | Remove shutdown tag from unit
40 | Verify the chilled & condenser water valves are in proper operating position
50 | Check for proper condenser and chilled water flow
60 | Start the chiller with associated chilled and condensing water valves
70 | Review control panel for proper operation and recorded fault histories
80 | Check system pressures and temperatures
90 | Check refrigerant levels
100 | Check capacity control
110 | Inspect for signs of refrigerant leakage
120 | Check for unusual noise and vibration
130 | Check overall condition of unit
140 | Record and log all operating parameters
150 | Test the chiller function in Auto mode in BMS (if applicable)
160 | Check all interlock devices with chiller including pumps and control valves
170 | Perform chemical or required cleaning for heat exchanger and coil in Start Up
180 | Check Unit For Proper Operation
190 | Visual inspect for loose or damaged components and visible leaks
200 | Inspect thermal insulation integrity
210 | Clean and paint as required
215 | *Perform the following tasking for major components of chiller if applicable*
220 | ***Compressor***
230 | Check Compressor Oil Level, add or replace as per manufacturer's recommendation
240 | Check Compressor Oil Temperature.
250 | Verify oil heater operation
260 | Check System Control Tests.
270 | Check Compressor For Excessive Noise/Vibration
280 | Perform compressor vibration test if app
290 | Perform oil analysis test for compressor oil
300 | Change purge filter dryers / strainers
310 | Assess field-serviceable bearings. Lubricate as needed
320 | ***Condenser***
330 | Inspect air-cooled condenser surfaces for damages. Repair or clean as needed
340 | Check fan blades & housing. Clean, repair or replace to ensure proper operation
350 | Inspect Cooler And Condenser Tubes For Leaks; Clean Screens As Necessary.
360 | Check fans for loose rivets and cracks, check motor bracket
370 | Check coil fins for damage and straighten as necessary
380 | Check for any fouling on heat exchange surface.
390 | ***Evaporator***
400 | Carry out mechanical evaporator tube brushing (if applicable)
410 | Use a nondestructive test to inspect condenser tubes if app (Eddy Current Test)
420 | ***Expansion Valve***
430 | Check the expansion valve sight glass to ensure sufficient refrigerant flow
440 | Recharge the refrigerant as per manufacturer's standard if required
450 | ***Electrical***
460 | Check contactors for pitting, replace as required
470 | Check terminal for tightness, tighten as necessary
480 | Clean control panel interior
490 | Visual inspect for components for sign of overheating
500 | Megger compressor motor
510 | Check all electrical interlocks and BMS control sequence if equipped
520 | Inspect built-in VFD condition (if applicable)
530 | ***Others***
540 | Lubricate and check capacity control and linkage
550 | Clean the strainers for chilled water pumps
560 | Document tasks performed during visit and report any deficiencies
570 | Review test report and follow up with contractor for any defects
580 | Update software / algorithm for proper operation as needed
590 | Findings reported to Maintenance Supervisor

## ACCH-M-01-R21
ACCH-M-01-R21 | MONTHLY AIR COOLED CHILLER INSPECTION (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Unit For Proper Operation
30 | Visual inspect for loose or damaged components and visible leaks
40 | Inspect thermal insulation integrity
50 | Clean and paint as required
60 | ***Compressor***
70 | Check Compressor Oil Level, add or replace as per manufacturer's recommendation
80 | Check Compressor Oil Temperature.
90 | Check Compressor For Excessive Noise/Vibration
100 | ***Condenser***
110 | Check fan blades and fan housing. Clean, repair or replace to ensure proper oper
120 | Inspect Cooler And Condenser Tubes For Leaks
130 | Check coil fins for damage and straighten as necessary
140 | Check for any fouling on heat exchange surface.
150 | ***Expansion Valve***
160 | Check the expansion valve sight glass to ensure sufficient refrigerant flow
170 | ***Electrical***
180 | Visual inspect for components for sign of overheating
190 | ***Others***
200 | Review control panel for proper operation and recorded fault histories
210 | Lubricate and check capacity control and linkage
220 | Check for proper condenser and chilled water flow
230 | Check system pressures and temperatures
240 | Check refrigerant levels
250 | Check capacity control and linkage
260 | Inspect for signs of refrigerant leakage
270 | Check for unusual noise and vibration
280 | Record and log all operating parameters
290 | Perform chemical or required cleaning for heat exchanger and coil if applicable
300 | Perform oil analysis tet for compressor oil if required
310 | Findings reported to Maintenance Supervisor

## WCCH-A-02-R21
WCCH-A-02-R21 | ANNUAL WATER COOLED CHILLER SHUTDOWN (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | ***Seasonal Shut-down***(Fall)
30 | Review control panel for proper operation and recorded fault histories
40 | Check refrigerant levels
50 | Record and log all operating parameters
60 | Shut down chiller and associated chilled and condensing water valves
70 | Conduct refrigerant leak check
80 | Tag chiller & cooling towers out of service
90 | Disable chiller & cooling tower function in BMS (if applicable)
100 | Findings reported to Maintenance Supervisor

## WCCH-A-01-R21
WCCH-A-01-R21 | ANNUAL WATER COOLED CHILLER STARTUP INSPECTION & CLEANING (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | ***Seasonal Start-up*** (Spring) - If applicable
30 | Remove shutdown tag from unit
40 | Verify the chilled & condenser water valves are in proper operating position
50 | Check for proper condenser and chilled water flow
60 | Start the chiller with associated chilled and condensing water valves
70 | Review control panel for proper operation and recorded fault histories
80 | Check system pressures and temperatures
90 | Check refrigerant levels
100 | Check capacity control
110 | Inspect for signs of refrigerant leakage
120 | Check for unusual noise and vibration
130 | Check overall condition of unit
140 | Record and log all operating parameters
150 | Test the chiller function in Auto mode in BMS (if applicable)
160 | Resume water treatment system and carry out water test for relevant parameters
170 | Perform chemical or req cleaning for heat exchanger & cooling tower in Startup
180 | Check Unit For Proper Operation
190 | Visual inspect for loose or damaged components and visible leaks
200 | Inspect thermal insulation integrity
210 | Clean and paint as required
220 | ***Compressor***
220 | Carry out mechanical condenser tube brushing (if applicable)
230 | Check Compressor Oil Level, add or replace as manufacturer's recommendation
240 | Check Compressor Oil Temperature.
250 | Verify oil heater operation
260 | Check System Control Tests.
270 | Check Compressor For Excessive Noise/Vibration
280 | Perform compressor vibration test
290 | Perform oil analysis test for compressor oil
300 | Change purge filter dryers / strainers
310 | Assess field-serviceable bearings. Lubricate as needed
320 | ***Condenser***
330 | Carry out mechanical condenser tube brushing
340 | Replace gasket if required
350 | Remove and dispose any debris from any maintenance activity
360 | Use a nondestructive test to inspect condenser tubes if app (Eddy Current Test)
370 | ***Evaporator***
390 | Use a nondestructive test to inspect evaporator tubes if app (Eddy Current Test)
400 | ***Expansion Valve***
410 | Check the expansion valve sight glass to ensure sufficient refrigerant flow
420 | Recharge the refrigerant as per manufacturer's standard if required
430 | ***Cooling Tower***
440 | Check water for clarity, odor, debris, algae & temp to prevent microbial growth
450 | Check internal surface condition for scale, rust, sludge & biofilm accumulation
460 | Check sprays and distribution deck for proper water distribution
470 | Check for proper operation of bleed-off valves and other valves accessories
480 | To check the control system
490 | To check the condition of water pan
500 | To check and clean strainer
510 | To check float valve operation
520 | To check fan motor & spinner
530 | To check bleed-off valve and conductivity measurement kit
540 | To check fan motor operation current
550 | To replace the fan belt if so required
560 | ***Water Basin (CT)***
570 | Check basin sides and corners of cooling towers for any leakage or overflow.
580 | Inspect suction screen and clean away any accumulated debris.
590 | Assure float valves & makeup controls operating freely with proper water level
600 | Water basin and internal surfaces of towers should be cleaned and disinfected
610 | ***Tower Framework (CT)***
620 | Inspect visually for any deterioration and test members for soft spots
630 | Remove corrosion and rust and carry out touch-up painting
640 | Inspect the general condition & check tightness of framework bolts for safe use
650 | ***Fills and Drift Eliminators (CT)***
660 | Check condition / cleanliness of fillers and drift eliminators & remove any dirt
670 | Check fills are intact and in place with no sagging or gaps in packs
680 | ***Others (CT)***
690 | Adjust and lubricate fans, pumps and motors bearings
700 | Adjust and lubricate all moving parts of valves
710 | Clean the water distribution pipework including nozzles
720 | High Jet cleaning for fillers & drift eliminators, manually clean the tower
730 | Fills and drift eliminators should be removed for cleaning
740 | End cap in each header should be removed for cleaning
750 | To check all motor bearing condition
760 | Report on general condition of unit and the necessity of overhauling services
770 | ***Electrical***
780 | Check contactors for pitting, replace as required
790 | Check terminal for tightness, tighten as necessary
800 | Clean control panel interior
810 | Visual inspect for components for sign of overheating
820 | Megger compressor motor
830 | Check all electrical interlocks and BMS control sequence if equipped
840 | Inspect built-in VFD condition (if applicable)
850 | ***Others***
860 | Lubricate and check capacity control and linkage
870 | Clean the strainers for Chilled & Condensing water pumps
880 | Document tasks performed during visit and report any deficiencies
890 | Review test report and follow up with contractor for any defects
900 | Update software / algorithm for proper operation as needed
910 | Findings reported to Maintenance Supervisor

## WCCH-M-01-R21
WCCH-M-01-R21 | MONTHLY WATER COOLED CHILLER INSPECTION (RFP)
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Unit For Proper Operation
30 | Visual inspect for loose or damaged components and visible leaks
40 | Inspect thermal insulation integrity
50 | Clean and paint as required
60 | ***Compressor***
70 | Check Compressor Oil Level, add or replace as per manufacturer's recommendation
80 | Check Compressor Oil Temperature.
90 | Verify oil heater operation
100 | Check System Control Tests.
110 | Check Compressor For Excessive Noise/Vibration
120 | *** Condenser***
130 | Check the condenser supply & return pressure & temperature
140 | ***Evaporator***
150 | Check the evaporator supply & return pressure & temperature
160 | ***Expansion Valve***
170 | Check the expansion valve sight glass to ensure sufficient refrigerant flow
180 | ***Cooling Tower***
190 | Check water for clarity, odour, debris, algae & temp to prevent microbial growth
200 | Check internal surface condition for scale, rust, sludge & biofilm accumulation
210 | Check sprays and distribution deck for proper water distribution
220 | Check for proper operation of bleed-off valves and other valves accessories
230 | To check the control system
240 | To check the condition of water pan
250 | To check and clean strainer
260 | To check float valve operation
270 | To check fan motor & spinner
280 | To check bleed-off valve and conductivity measurement kit
290 | To check fan motor operation current
300 | To replace the fan belt if so required
310 | ***Water Basin (CT)***
320 | Check basin sides and corners of cooling towers for any leakage or overflow.
330 | Inspect suction screen and clean away any accumulated debris
340 | Assure float valves & makeup controls operating freely with proper water level
350 | ***Fills and Drift Eliminators (CT)***
360 | Check condition / cleanliness of fillers & drift eliminators, remove any dirt
370 | Check fills are intact and in place with no sagging or gaps in packs
380 | ***Electrical***
390 | Visual inspect for components for sign of overheating
400 | Check all electrical interlocks and BMS control sequence if equipped
410 | Inspect built-in VFD condition (if applicable)
420 | ***Others***
430 | Review control panel for proper operation and recorded fault histories
440 | Lubricate and check capacity control and linkage
450 | Check for proper condenser and chilled water flow
460 | Check system pressures and temperatures
470 | Check refrigerant levels
480 | Check capacity control and linkage
490 | Inspect for signs of refrigerant leakage
500 | Check for unusual noise and vibration
510 | Record and log all operating parameters
520 | Findings reported to Maintenance Supervisor

## HRU-A-02-R21
HRU-A-02-R21 | ANNUAL HEAT RECOVERY UNIT INSPECTION (RFP)
Sequence | Description
10 | Complete Pre Job Hazard Assessment
20 | Vacuum, wash and inspect standard foam filters
30 | Wash the foil faced insulation surface and wipe the drain pan
40 | Check for proper operation of heat exchanger and clean
50 | Check and clean blower wheels and fan housing
60 | Check all control modes for proper operation
70 | Check damper for proper operations, condition and setting and adjust as needed
80 | Check fan belt tension
90 | Assess field serviceable bearings and Lubricate
100 | Check P-trap drain and Clean
110 | Report any corrosive and damaged surface
120 | Findings Reported To City Representative

## HRU-Q-01
HRU-Q-01 | QUARTERLY HEAT RECOVERY UNIT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Clean air filters
30 | Clear the exterior intake and exhaust vents of obstructions
40 | Clean the heat-exchange core
50 | Clean the condensate drain and pan
60 | Findings Reported To Facility Operation Supervisor

## EL-CB-MV-A
EL-CB-MV-A | ANNUALLY MEDIUM VOLTAGE POWER CIRCUIT BREAKERS INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Exercise periodically breakers tot ensure smooth operation and alignment
50 | Several manual open-and-close operation at set intervals
60 | Inspect breakers for cleanliness, anchorage, alignment and proper grounding
70 | Verify cell fit, alignment and racking mechanism operation
80 | Function test and verify all mechanism operated contacts and truck operated contact, if equipped
90 | Exercise electrically operated circuit breakers by their control power systems
100 | Verify mechanism charge, trip-free and anti-pump functions
110 | ***Electrical Testing***
120 | Test breakers for insulation resistance
130 | Perform power factor test as required
140 | Test breakers contact /poles for contact resistance
150 | Inspect bolted connections
160 | Findings Reported To Maintenance Supervisor

## EL-CA-A
EL-CB-A | ANNUALLY POWER CABLES INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Inspect for signs of physical damage
50 | Inspect for loosen screw, bolts and nuts
60 | Note evidence of overheating
70 | Inspect for discolored, cracked or brittle insulation or jacket
80 | Verify that cable bends meet or exceed min. bending radius
90 | Inspect for signs of corrosion, discoloration, oxidation of metallic shield
100 | Inspect shield grounding and cable support
110 | Note signs of corona
120 | ***Electrical Testing***
130 | Perform insulation resistance test
140 | Perform shield continuity test
150 | Inspect bolt connections
160 | Findings Reported To Maintenance Supervisor

## EL-TX-DRY-A
EL-TX-DRY-A | ANNUALLY DRY-TYPE POWER TRANSFOMER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Verify the oil levels, temperature, pressures, note max. reading and reset gages
50 | Inspect anchorage and grounding
60 | Inspect condition of windings, core assembly, shims and insulation.
70 | Note any losse, borken or deteroriated parts
80 | Inspect and function test resistance or impedance grounding system, if equipped
90 | Verify the presence of surge arrestors
100 | ***Electrical Testing***
110 | Perform insulation resistance test, from high-side to low-side winding and windings to ground, Calculate PI.
120 | Perform turns-ratio test on designate tap setting
130 | Perform power factor test for all windings
140 | Perform winding-resistance test on required tap positions
150 | Inspect bolt connections
160 | Findings Reported To Maintenance Supervisor

## EL-TX-LQ-A
EL-TX-LQ-A | ANNUALLY LIQUID FILLED POWER TRANSFORMER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer Z463-18 Maintenance of Electrical System - Chapter 8 requirement for inspection
30 | ***Visual and mechanical test***
40 | Verify the oil levels, temperature, pressures, note max. reading and reset gages
50 | Inspect the transformer and all associated instrumentation and control equipment for damage
60 | Inspect main tank, conservator tank and radiators for leaking or staining, corrosion or peeling paint
70 | Verify the presence of PCB labelling
80 | Inspect anchorage and grounding
90 | Inspect condition of breather assemblies, if equipped
100 | Function of mechanical accessories such as oil lever gages, temp gages and pressure relief device
110 | Test operation of cooling fans and oil circulating pumps, if equipped
120 | Clean bushings and control cabinets
130 | Inspect and function test resistance or impedance grounding system, if equipped
140 | Verify the presence of surge arrestors
150 | Remove a sample of insulating liquid and test fluid quality with ANSI/IEEE C57.106
160 | Remove a sample of insulating liquid and test and measure dissolved gases with ANSI/IEEE C57.104
150 | ***Electrical Testing***
160 | Perform insulation resistance test, from high-side to low-side winding and windings to ground, Calculate PI.
170 | Perform turns-ratio test on designate tap setting
180 | Perform power factor test for all windings
190 | Perform power factor test on bushings if equipped with capacitance tap
200 | Perform winding-resistance test on required tap positions
210 | Inspect bolt connections
220 | Findings Reported To Maintenance Supervisor

## FA-A-01
FA-A-01 | Annual Fire Alarm Inspection
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | As per CAN/ULC-S537, Standard for Vertification of Fire Alarm system for annual inspection
30 | ***CONTROL UNIT OR TRANSPONDER TEST***
31 | Power "ON" visual indicator operates
32 | Common visual trouble signal operates
33 | Trouble signal silence switch operates
34 | Trouble signal silence switch operates
35 | Main power supply failure trouble signal operates
36 | Ground fault tested for positive and negative indication initiates trouble signal
37 | Alert signal operates
38 | Alarm signal operates
39 | Automatic transfer from alert signal to alarm signal operates. Time: _________
40 | Manual transfer from alert signal to alarm signal operates
41 | Automatic transfer from alert signal to alarm signal cancel (acknowledge) feature operates on a two-stage system
42 | Alarm signal silence inhibit function operates
43 | Alarm signal manual silence operates
44 | Alarm signal silence visual indication operates
45 | Alarm signal and visible signal devices, when silenced, automatically reinitiate upon subsequent alarm
46 | Alarm signal silence automatic cut-out timer
47 | Audible and visual alarm signals programmed and operate per design and specification
48 | Input circuit, alarm and supervisory operation, including audible and visual indicator operates
49 | Input circuit supervision fault caused a trouble indication
50 | Output circuit alarm indicator operates
51 | Output circuit supervision faulty causes a trouble indication
52 | Visible indicate test (Lamp test) operates
53 | Code signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter
54 | Code signal sequences operate are not interrupted by subsequent alarms
55 | Ancillary device control circuit is rated for the intended purpose
56 | Ancillary device by-pass results in trouble signal
57 | Input circuit to output circuit operation, including ancillary device circuits for correct program operation, as per design and specification
58 | Fire alarm system reset operates
59 | Main power supply to emergency power supply transfer operates
60 | Control unit or transponder bonded to ground
61 | Status change confirmation feature (Smoke detectors only) verified
62 | Receipt of the alarm transmission to the fire signal receiving centre
63 | Receipt of the supervisory transmission to the fire signal receiving centre
64 | Receipt of the trouble transmission to the fire signal receiving centre
65 | Record the name and the telephone number of the fire signal receiving centre
66 | Operation of the fire alarm signal receiving centre disconnect means results in a specific trouble indication at the control unit or transponder and transmit a trouble signal to the fire signal receiving centre
67 | **VOICE COMMUNICATE TEST***
68 | Power "ON" indicator operates
69 | Common visual trouble signal operates
70 | Common audible trouble signal operates
71 | Trouble signal silence switch operates
72 | All-call voice paging, including visual indicator, operates
73 | Output circuits for selective voice paging, including visual indication, operates
74 | Output circuits for selective voice paging trouble operation, including visual indication, operates
75 | Microphone, including press to talk switch, operates
76 | Operation of voice paging does not interfere with initial inhibit time of alert or alarm signal
77 | All-call voice paging operates (on emergency power supply)
78 | Upon failure of one amplifier, system automatically transfer to backup amplifier
79 | Circuits for emergency telephone call-in operation, including audible and visual indication operates
80 | Circuit for emergency telephone for operation, including 2-way voice communication, operates
81 | Circuits for emergency telephone trouble operation, including visual indication, operates
82 | Emergency telephone verbal communication operates
83 | Emergency telephone operable or in-use tone at handset operates
84 | Test voice communication busses in standby mode
85 | ***CONTROL UNIT OR TRANSPONDER INSPECTION***
86 | Control unit or transponder location:
87 | Control unit or transponder identification:
88 | Input circuit designations correctly identified in relation to connected field devices
89 | Output circuit designations correctly identified in relation to connected field devices
90 | Correct designations for common control functions and indicators
91 | Plug-in components and modules securely in place
92 | Plug-in cables securely in place'
93 | Record the date, revision and version of firmware and software program
94 | Clean and free of dust and dirt
95 | Fuses in accordance with manufacturer's specification
96 | Control unit or transponder lock functional
97 | Termination points from wiring to field device secure
98 | ***POWER SUPPLY INSPECTION***
99 | Control unit or transponder location:
100 | Control unit or transponder identification:
101 | Fuses in accordance with manufacturer's specification
102 | Adequate to meet the requirement of the system
103 | ***EMERGENCY POWER SUPPLY TEST AND INSPECTION***
104 | Control unit or transponder location:
105 | Control unit or transponder identification:
106 | Correct battery type as recommended by manufacturer
107 | Correct battery rating as determined by battery calculations based on full system load
108 | Battery voltage with main power supply "ON"
109 | Battery voltage and current with main power supply "OFF" and fire alarm system in supervisory condition
110 | Voltage: ________V dc
111 | Current: ________A dc
112 | Battery voltage and current with main power supply "OFF" and fire alarm system in full load condition
113 | Voltage: ________V dc
114 | Current: ________A dc
115 | Charging current on a fully charged battery
116 | Inspected for physical damage
117 | Terminals cleaned and lubricated
118 | Terminal clamped tightly
119 | Specific gravity of the electrolyte is within manufacturer's specification
120 | Electrolyte leakage
121 | Adequately ventilated
122 | Record manufacturer's date code or in-service date
123 | Disconnection causes trouble signal
124 | Indicate type of battery test performed on a fully charged battery
125 | i) Required supervisory load for 24h followed by the required full load operation; or
126 | ii) A silent test by using the load resistor method may be used for the full duration test; or
127 | iii) Silent accelerated test; or
128 | iv) A battery capacity meter test; or
129 | v) In lieu of the above battery tests, replace the battery with a new set having a current date code, amp-hour capacity and type
130 | Record calculated battery capacity
131 | Record battery terminal voltage after completion of tests
132 | Battery voltage not less than 85% of its rating after the tests
133 | Generator provides power to the AC circuit serving the fire alarm system
134 | Trouble condition at the generator results in an audible common trouble signal and a visual indication at the require annunciator
135 | ***ANNUNCIATOR, REMOTE TROUBLE SINGAL UNIT TEST AND INSPECTION***
136 | Annunciator or sequential display location:
137 | Annunciator or sequential display identification:
138 | Power "ON" indicator operates
139 | Individual alarm and supervisory input zone clearly indicated and separately designated
140 | Individual alarm and supervisory input zone designation labels are properly identified
141 | Common trouble signal operates
142 | Visual indicator test (Lamp test) operates
143 | Input wiring from control unit or transponder is supervised
144 | Alarm signal silence visual indication operates
145 | Switches for ancillary functions operates as per design and specification
146 | Other ancillary function visual indicators operate
147 | Manual activation of alarm signal and indication operates
148 | Displays are visible in installed location operates
149 | Operates on emergency power
150 | ***ANNUNCIATORS OR SEQUENTIAL DISPLAYS***
151 | Annunciator or sequential display location:
152 | Annunciator or sequential display identification:
153 | Power "ON" indicator operates
154 | Individual alarm and supervisory zone indication operates
155 | Exception: Operation on each individual alarm and supervisory zone indication
156 | Specify method of confirmation
157 | Minimum of one alarm zone and one supervisory zone tested per annunciator or sequential display to confirm operation
158 | Individual alarm and supervisory zone designation labels are properly identified
159 | Common trouble signal operates
160 | Visual indicator test (Lamp test) operates
161 | Input wiring from control unit or transponder is supervised
162 | Alarm signal silence visual indication operates
163 | Switches for ancillary functions operates as per design and specification
164 | Other ancillary function visual indicators operate
165 | Manual activation of alarm signal and indication operates
166 | Displays are visible in installed location operates
167 | ***REMOTE TROUBLE SIGNAL UNIT TEST AND INSPECTION***
168 | Input wiring from control unit or transponder is supervised
169 | Visual trouble signal operates
170 | Audible trouble signal operates
171 | Audible trouble signal silence operates
172 | ***PRINTER TEST***
173 | Operates as per design and specification
174 | Zone of each alarm initiating device is correctly printed
175 | Rated voltage is present
176 | ***DATA COMMUNICATION LINK TEST***
177 | Control unit or transponder location:
178 | Control unit or transponder identification:
179 | Data communication link identification:
180 | Confirm that a trouble signal is received under open loop fault
181 | Fault isolation modules are installed in Data communication link serving Field devices
182 | Fault isolation in Data communication link is provided between control unit and transponders
183 | ***ANCILLARY DEVICE CIRCUIT TEST***
184 | Record specific type of ancillary circuit
185 | ***INTERCONNECTION TO THE FIRE SIGNAL RECEIVING CENTRE
186 | The fire signal receiving centre transmitting is integral to the fire alarm control unit
187 | An interconnection between the fire alarm control unit and a separate fire signal receving centre transmitted is provided
188 | Where an interconnection between the fire alarm control unit and a separate fire signal receiving centre transmitter is provided with a demarcation terminal box
189 | The demarcation terminal box is located in the same room as the fire alarm control unit is connected to
190 | The demarcation terminal box is labeled "Fire Alarm Demarcation"
191 | Test and confirmed operation of fire relay
192 | Test and confirmed opeation of trouble relay
193 | Test and confirmed operation of supervisory relay
194 | Confirm that the fire alarm transmission to the fire signal receiving centre is received
195 | Confirm that the supervisory tranmission to the fire signal receiving centre is received
196 | Confirm that a trouble transmission to the fire signal receiving centre is received
197 | Operation of the fire alarm receiving centre transmitter bypass means results in trouble indication at the control unit
198 | Operation of the fire signal receiving centre transmitter bypass means transmits a trouble signal to the fire signal receiving centre
199 | Record the name and the telephone number of the fire signal receiving centre
200 | ***FILL IN INDIVIDUAL DEVICE RECORD***
201 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM
Sequence | Description
10 | Fire Alarm System Tested Pass Fail
20 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
30 | Pre Job Hazard Assessment Completed?

## EG-A-01
EG-A-01 | ANNUAL EMERGENCY GENERATOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer To CSA C282-15 for Emergency Generator Annual Inspection
30 | Weekly, Monthly and Semi Annually Check Complete
40 | ***Control panel***
50 | Open all inspection covers and inspect all electrical connections.
60 | Test breakers for proper operation.
70 | Clean insulators and bushings.
80 | Test voltage regulator for proper operation.
90 | Operate all moving parts to ensure that they move freely.
100 | Clean and dress contacts as necessary.
110 | Remove all dust.
120 | Conduct infrared survey of electrical connections at full load (if applicable)
130 | To identify any high-resistance connections
140 | ***Engine***
150 | Change engine lubrication oil and filters.
160 | Test strength of coolant and chemical protection level of coolant inhibitors.
170 | Change fuel filters, clean strainer(s), and verify that the fuel supply is open.
180 | Inspect, check and record the back pressure of the exhaust system
190 | Clean and lubricate linkages.
200 | Inspect air filters.
210 | Inspect all mechanical connections.
220 | Inspect all electrical connections.
230 | Inspect all external surfaces of heat exchanger(s) and clean as necessary.
240 | Inspect all belts and hoses and replace if necessary.
250 | Test and inspect ignition system(s). Replace any defective components.
260 | Inspect coolant pump(s) for leaks and external wear
270 | ***Diesel fuel storage tank(s)***
280 | Drained and refilled with fresh fuel as per National Fire Code (6.7.1.5) or
290 | Full filtered to remove water, scale, bacteria to minimize filter clogging
300 | The bottom(s) of the tank(s) shall be also tested chemically for water.
310 | ***Generator***
320 | Test surge suppressor and rotating rectifier on brushless machines.
330 | Grease bearings (replace old grease with new) (if applicable).
340 | Clean commutator and slip rings (if applicable).
350 | Clean rotor and stator windings using clean compressed air.
360 | Inspect coupling bolts and alignment.
370 | Inspect conduits for tightness.
380 | Inspect windings at rotor and stator slots.
390 | Inspect all electrical connections.
400 | ***Overcurrent Protective Device***
410 | Electrically isolate all overcurrent protective devices
420 | Remove all dust.
430 | Test devices for proper operation
440 | ***Transfer switches***
450 | Isolate transfer switch, open all inspection covers, and inspect all electrical
460 | Operate all moving parts to ensure that they move freely.
470 | Clean and dress contacts as required.
480 | Remove all dust.
490 | Clean and lubricate linkages.
500 | ***Others***
510 | Lubricate door locks and hinges (if necessary), especially of outdoor enclosures
520 | Conduct a 2 h full-load test (see Clause 11.3).
530 | Correct all the defects found during inspections and tests.
540 | Record all inspections, tests, and corrective actions in the log
550 | Check internal engine thermostat of the coolant system, replace as needed
560 | Check proper function of room thermostat of generator room if applicable.
570 | Record all required measured parameters
580 | Review and rectify defects in inspection report by contractor
590 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM | Description
10 | Refer To Canadian Standards Association (Csa) For Emer Generator Annual Insp.
20 | Csa Standard No. C282-15 -- Emergency Electrical Power Supply For Building
30 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
40 | Pre Job Hazard Assessment Completed?

## EG-S-01
EG-S-01 | SEMI-ANNUAL - EMERGENCY GENERATOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CSA C282-15 for Emergency Generator Semi-Annually inspection
30 | Weekly and Monthly Check Complete
40 | Inspect and clean engine crankcase breathers.
50 | Inspect and clean all engine linkages
60 | Lubricate the engine governor and ventilation system.
70 | Test protective devices for proper operation.
80 | Perform two full cranking cycles specified in Clauses 7.5, 10.4.1, 10.4.2
90 | Measure and record lowest battery voltages while cranking
100 | Replace the battery if the measured voltage is less than 80%
110 | Or perform a battery load test using a suitable load tester as alternative
120 | Inspect ventilation system belt(s).
130 | Correct all defects found during inspections and tests.
140 | Record all inspections, test, and corrective actions in the log
150 | Findings Reported To Maintenance Supervisor
Exsiting tasks in EAM
10 | Refer To Canadian Standards Association (Csa) For Emer Generator Annual Insp.
20 | Csa Standard No. C282-15 -- Emergency Electrical Power Supply For Building
30 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
40 | Pre Job Hazard Assessment Completed?

## EG-M-01
EG-M-01 | MONTHLY EMERGENCY GENERATOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CSA C282-15 for Emergency Generator monthly inspection
30 | Weekly Check Complete
40 | ***Test and verify the entire system as follows***
50 | Simulate a failure of the normal electrical supply to the building.
60 | Verify battery charger current output increase while cranking
70 | Operate the system under at least 30% of the rated load for 60 min.
80 | Operate all automatic transfer switches under load.
90 | Inspect brush operation for sparking, if applicable
100 | Inspect for bearing seal leakage.
110 | Inspect for correct operation of all auxiliary equipment as follows:
120 | Radiator shutter Control
130 | Coolant Pumps
140 | Fuel Transfer Pumps
150 | Oil Coolers
160 | Engine room ventilation system
170 | Record the readings for all instruments in the log and verify normal or not
180 | Drain the exhaust system condensate trap.
190 | Inspect block heater hoses and wires.
200 | Correct all defects found during inspections and tests.
210 | Record all inspections, tests, and corrective actions in the log
220 | Inspect all electrical components to ensure proper function
230 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM
10 | Refer To Canadian Standards Association (Csa) For Emergency Gen Monthly Insp.
20 | Csa Standard No. C282-09 -- Emergency Electrical Power Supply For Buildings
30 | Weekly Check Complete
40 | Operating Hrs. (Before)
50 | Start Time
60 | Load Transfer To Emerg. (Secs)
70 | Ac Volts
80 | Ac Amps
90 | Hertz
100 | Engine Oil Pressure
110 | Engine Coolant Temperature
120 | Engine Rpm
130 | Gas Pressure
140 | Diesel Fuel Pressure
150 | Battery Voltage
160 | Kw
170 | Kva
180 | Total Kw
190 | Kw Hours
200 | % Load
210 | Louver(S) Position
220 | Fire Panel Annunciation
230 | Check For Leaks
240 | Load Transfer To Utility (Secs)
250 | Engine Cooldown (Secs)
260 | Trans. Sw./Gen In Auto
270 | Operating Hrs. (After)
280 | Fire Extinguisher Check
290 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
300 | Pre Job Hazard Assessment Completed?

## PU-FI-A-01
LS-FI-PU-A | ANNUALLY FIRE PUMP INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NFPA 25 Standard - Chapter 8 (8.1-8.3) requirement for inspection
30 | ***General Inspection***
40 | Inspect cable / wire insulation | 8.3.6.4
50 | Inspect engine crankcase breather | 8.1.1.2.12
60 | Inspect exhuast system and drain condensate trap | 8.1.1.2.13
70 | Inspect flexible hoses and connections | 8.1.1.2.11
80 | Inspect fuel tank vents and overflow if equipped | 8.1.1.2.10
90 | Inspect shaft movement while running | 8.1.1.2.1
100 | Inspect the suction screen and clear of any debris | 8.3.3.12
110 | ***Test***
120 | Test diesel fuel for any degradation. Correct as needed | 8.3.4
130 | Conduct annual flow testing and pump performance | 8.3.3
140 | Activate fire alarm circuits including local and remote alarm indicating devices | 8.3.3.10
150 | Test backup electronic module (ECM) with associated sensors if equipped | 8.3.3.13
160 | Test the main relief valve | 8.3.3.8
170 | Test the function overcurrent protective devices when triggering the ATS | 8.3.3.9
180 | Check fuel tank, float switches and supervisory signal if equipped | 8.1.1.2.7
190 | Check supevisory signal circuitry for high cooling water temperature if equipped | 8.1.1.2.8
200 | ***Maintenance***
210 | Check battery condition and clean the terminals of any corrosion | 8.1.1.2.15
220 | Replace circulation water filter if equipped | 8.1.1.2.20
230 | Check all control and power wiring connection | 8.1.1.2.16
240 | Change lubrication oil in engines | 8.1.1.2.17
250 | Change lubrication oil filter | 8.1.1.2.18
260 | Check fuel tanks for water and foreign materials | 8.1.1.2.9
270 | Measure back pressure on the engine turbos if equipped | 8.1.1.2.14
280 | Inspect the accuracy of pressure gauages and sensors | 8.1.1.2.21
290 | Grease pump and motor bearings and couplings | 8.1.1.2.3
300 | Check the condition of sacrificial anodes, replace as needed | 8.1.1.2.19
310 | Record any deficiencies and submission of test report
Existing Task | PU-I-03
10 | Under No Circumstances Will The Fire Panel Be Left Unattended While Bypassed
20 | System Pressure
30 | City Pressure
40 | Open Test Valve Slowly
50 | Jockey Pump Cut-In Pressure
60 | Turn Off Jockey Pump
70 | Fire Pump Cut-In Pressure
80 | Close Test Valve
90 | Allow Fire Pump To Run 10 Minutes (On Timer)
100 | Turn Jockey Pump Back To Auto
110 | Jockey Pump To Run 2 Minutes (On Timer)
120 | Verify Relief Valves Open (2)
130 | Verify Fire Pump Run Status On Fire Panel-Check Bearing Packing
140 | Verify Fire Pump Run Status On Fire Panel-System Pressure (During Test)
150 | Verify Fire Pump Run Status On Fire Panel-Return Jockey Pump To Auto
160 | System Pressure (After Test)
170 | City Pressure (After Test)
180 | Reset Fire Panel And Turn Off Bypasses
190 | Bocc To Go Back Online: Electrician To Turn On/Off Bypasses On Fire Alarm Panel.
200 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
210 | Pre Job Hazard Assessment Completed?

## FE-A-01
FE-A-01 | ANNUALLY FIRE EXTINGUISHER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NFPA 10 Standard - Chapter 7 requirement for inspection
30 | Check any damages, corrosion or nozzle blockage
40 | A new listed tamper seal shall be installed
50 | Check conductivity of hose assemblies for CO2 extinguisher
60 | Conduct hydrostatic test as per manufacturer's instruction
70 | Recharging the extinguisher if needed
80 | A tag or label securely attached with extinguisher
90 | Identify month and year maintenance
100 | Person performing the work
110 | Name of agency perfrom the work
120 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM
Sequence | Description
10 | Inspect, Test & Recharge All Fire Extinguishers In Building
20 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
30 | Pre Job Hazard Assessment Completed?

## AED-01
AED-01 | QUARTERLT AUTOMATED EXTERNAL DEFIBRILLATOR INSPECTION
Sequence | Description
10 | Check readiness display for OK indicator
20 | CHRGE-PAK indicator: Replace CHRGE-PAK Battery Chrge/ QUIK-PAK Electrode Packet
30 | ATTENTION indicator: Refer to operating instructions
40 | WRENCH indicator: Contact authorized service personnel
50 | Chk expire dates on all electrd pad: Replace electrd pad & CHRGE-PA if date pass
60 | Check additional supplies: Replenish as needed
70 | Check AED for: Damage or cracks: Contact authorized service personnel
80 | Check AED for Foreign substances: Clean the device
90 | Check the functionality of the audible alarm of the AED containment box.
100 | Check the inventory of the "Additional supplies" inside the accessories bag, rep
110 | Verify: S/N, Model Make, Battery Status, Battery Expiry,Inspect date, Phys Loc.

## AED-M-01
AED-M-01 | Monthly Auotmated External Defibrillator Inspection
Sequence | Description
10 | AED Readiness indicator displaying green or "OK"
20 | AED pads attached in unopened pouch and free of damage or foreign debris
30 | Battery Pack installed in AED
40 | No "errors" or "Alarms" noted
50 | Spare pads in AED carrying case pouch or under cover
60 | Pediatric Pads/Key/Switch present
70 | Kit complete and attached to the AED
80 | Kit includes Pocket Mask-1, Disp. Gloves-2, Razor-1, Scissor-1, Towel-1
90 | Check battery alarm and replace every 12 months
100 | Log-in to AHS portal site to document the inspection and submit

## LS-ATS
ATS-A-01 | ANNUAL TRANSFER SWITCH INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer To CSA C282-15 for Emergency Electrical Power Supply for Buildings
30 | Isolate Transfer Switch, open all inspection covers &
40 | Inspect all electrical connections
50 | Operate all moving parts to ensure that the move freely
60 | Clean and dress contacts as required
70 | Remove all dust
80 | Clean & lubricate all linkages
90 | Conduct an Infrared Survey of all electrical connections, contacts & energized
100 | components while under load on both the normal & the emergency side
110 | Findings Reported To Facility Operation Supervisor
ANNUALLY AUTOMATIC TRANSFER SWITCH INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CSA C282-15 & CSA-Z463-18 (8.2.24) requirement for inspection
30 | All workers must wear suitable personal protective equipment before inspection
40 | Isolate transfer switch, open all inspection covers, and inspect all electrical connections
50 | Operate all moving parts to ensure that they move freely.
60 | Clean and dress contacts as required.
70 | Remove all dust.
80 | Clean and lubricate linkages.
90 | Checking of connections
100 | Inspection or testing for evidence of overheating and excessive contact erosion
110 | Replacement of contacts when required
120 | Exercise all timers and relays for proper function
130 | To carry out thermographically scan (if applicable)
140 | Check seated plug-in connectors in accordance with design
150 | Perform insulation resistance test from phase terminals to case for 1 min and verify with maufacturer's value
160 | Energized components while under load on both the normal and the emergency side.
170 | Electrically operating the transfer switch from primary position to alternate position
180 | Return to primary position after test
190 | Findings reported to Maintenance Supervisor

## LS-FD
LS-FD | ANNUAL FIRE DAMPER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to NFPA 80 - Chapter 19 requirement for inspection
30 | All workers must wear suitable personal protective equipment before inspection
40 | Inspect dampers are in place and not obviously damaged or obstructed
50 | Inspect the condition of fusible link, replace as needed
60 | Visually confirm the damper is in full-open or full close required by the design
70 | Command and visually confirm the damper to full close or full-open position
80 | Restore and visually confirm the damper to original operating position after test
90 | Lubricate all moving parts as per manufacturer's instruction
100 | Repair the damper at once if it is not operable
110 | Record the inspection date, inspector and deficienices
120 | Findings Reported To Maintenance Supervisor

## PD-POOL-WT-W
PD-POOL-WT-W | WEEKLY POOL CHEMICAL WATER TREATMENT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | All preventative maintenance to be performed as per Pool Standard of Alberta Health
30 | Molybdenum shall be maintained between 80 to 100 ppm
40 | pH shall be maintained between 6.8 and 7.6
50 | Record the Conductivity/TDS level
60 | Test the free chlorine level, should be maintained at least 2.0 mg/L
70 | Record the Oxidation Reduction Potential (ORP) level, no less than 770mV
80 | Total alkalinity shall be maintained between 60-180 mg/L
90 | Visual report on water clarity and suspended solids
100 | Inspect and record make up water meter reading
110 | Record all measurement data in log book
120 | Inspect and replace inline cartridge filters and O rings
130 | Provide and update all MSDS sheets on site
140 | Collect all pool water samples to AHS for analysis

## PD-POOL-FS-W
PD-POOL-FS-W | WEEKLY SAND FILTER INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Clean and clear the skimmer of debris, leaves, etc.
30 | Turn the pump off. Clean and empty the debris in strainer.
40 | Ensure that the "cut-off" valve is open if applicable
50 | Open the backwash valves and turn on the pump.
60 | Run the pump and see the sand start to rinse which can be seen in the sight glass.
70 | Run until water runs clear. (As per the time advised by manufacturer)
80 | Turn the pump off and close the backwash valves.
90 | Turn the pump back on.
100 | Adjust the frequency of VFD if needed
110 | Record the date and time in log book
120 | Sand in filter should be changed in every 2 years on heavily used pool (if applicable)

## PD-PL-WT-D
PD-POOL-WT-D | DAILY POOL CHEMICAL WATER TREATMENT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Test the free chlorine, combined chlorine and pH
30 | Monitor and record the automated readings and setpoint
40 | Compare the manual water test result with automated controller readings
50 | Rectify or adjust as needed

## PD-RO-A
PD-RO-A | ANNUAL REVERSE OSMOSIS SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Test RO feed water TDS, chlorine and water hardness content
30 | Check and set pretreatment filter and water softener clocks
40 | Log RO pump pressure, flow rate and temperature
50 | Test RO product water TDS and log flow rates
60 | Test RO reject water TDS and log flow rates
70 | Log Recovery % and Rejection %
80 | Log pressure gauge readings.
90 | Change RO pre-filters
100 | Check salt/ chemical tank levels and add as needed.
110 | Repair any minor leaks. Update PM Logs.
120 | Check for hardness and chlorine in RO feed water
130 | Check RO water TDS, temperature, pressure and flow rate
140 | Check all controls and adjust if needed
150 | Findings Reported To Maintenance Supervisor

## Life Safety Explanation
Equipment | Explanation | Code | Comment
Fire Alarm | A fire alarm system shall be installed in buildings in which an automatic sprinkler system is installed. | National Building Code 3.2.2.4 | Fulfilled
Clean Agent System | Clean agents fire suppression system are designed specifically to protect sensitive electronic equipment. Clean agents deploys quickly and cleanly - it won't leave behind oily residue, particulate or water. They are one of the fastest suppression systems available. It is often found in data centers, IT Server rooms, telecommunication facilities and other tech businesses. | NFPA 2001 | Not applicable to Park's Buildings
Fire Damper | Fire damper means a closure consisting of a damper that is installed in an air distribution system or a wall or floor assembly and that is normally held open but designed to close automatically in the event of a fire in order to maintain the integrity of the fire separation. | NFC 2019 2.2.2.4 | Visitor Centres might be applied subject to site verification
a) inspected at intervals not greater than 12 months to ensure that they are in place and not obviously damaged or obstructed, and
b) tested in accordance with NFPA 80, “Fire Doors and Other Opening Protectives
Standpipe System | a) more than 3 storeys in building height, | NBC 2019 3.2.5.8 | Not applicable to Park's Buildings
b) more than 14 m high measured between grade and the ceiling of the top storey, or
c) not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.5.8. for the applicable building height unless the building is sprinklered throughout.
Fire Sprinklers | Class I - Noncombustible products in ordainary cartons or in ordinary paper wrapping | The NFPA 13, Standard for the Installation of Sprinkler Systems
| Class II - Class I product in slatted wooden crates, solid wooden box, multiple thickness paperboard cartons | Chapter 4, General Requirement
Class III - A wood, paper, natural fibre, cloth or Group C plastics
Class IV - Class I, II or III products in corrugated cartons, containing Group A or B plastics
Group A plastics include acrylic, butyl rubber, fibreglass reinforced polyster, natural rubber and etc
Group B plastics include cellulosics, fluoroplastics, natural rubber (not expanded), nylon and silicone rubber
Group C plastics include fluoroplastics, malamine, phenolic resins, rigid PVC and urea formaldehyde
The following shall be protected with light hazard occupancy criteria in this standard:
4.3.2 * Light Hazard
(1) Spaces with low quantity and combustibility of contents
4.3.3 * Ordinary Hazard (Group 1).
The following shall be protected with OH1 occupancy criteria in this standard:
(1) Spaces with moderate quantity and low combustibility of contents
(2) Stockpiles of contents with low combustibility that do not exceed 8 ft (2.4 m)
4.3.4 * Ordinary Hazard (Group 2).
The following shall be protected with OH2 occupancy criteria in this standard:
(1) Spaces with moderate to high quantity and combustibility of contents
(2) Stockpiles of contents with moderate to high combustibility that do not exceed 12 ft (3.7 m)
4.3.5 * Extra Hazard (Group 1) (EH1).
The following shall be protected with EH1 occupancy criteria in this standard:
(1) Spaces with very high quantity and combustibility of contents
(2) Spaces where dust, lint, or other materials are present, introducing the probability of rapidly developing fires
4.3.6 * Extra Hazard (Group 2) (EH2).
The following shall be protected with EH2 occupancy criteria in this standard:
(1) Spaces with very high quantity and combustibility of contents
(2) Spaces with substantial amounts of combustible or flammable liquids
(3) Spaces where shielding of combustibles is extensive
| (1) One sprinkler shall be located at the top of each vertical riser and at the midpoint of each offset. Additional sprinklers shall be spaced on 24 ft (7.3 m) centers if the rise is greater than 24 ft (7.3 m). | Chapter 26 - Design Requirement
(2) Horizontal exhaust ducts shall have sprinklers located on 12 ft (3.7 m) centers beginning no more than 6 ft (1.7 m) from the duct entrance.
(3) If exhaust ducts are manifolded, a sprinkler shall be located in the manifold at the junction of each exhaust duct with the manifold.
(4) Sprinklers shall provide a minimum flow of 30 gpm (114 L/min) per head at a minimum of 15 psi (1 bar) pressure.
(5) Sprinklers shall be ordinary temperature rated, unless required to be higher due to operating temperatures measured in the ducts, in which case the operating temperature shall be at least 50°F (28°C) above the inside temperature of the duct.
(6)* The system demand shall include the discharge from the hydraulically most remote adjacent sprinklers in a common 100 linear ft (30.5 m) area of duct (horizontal and/or vertical).
(7)* The supply line to the duct sprinklers, if taken from the ceiling sprinkler system, shall be equipped with an accessible listed control valve.
Fire Extinguisher for Ordinary Hazard Occupancy | Minimum rated single extinguisher: 2-A | NFPA 10 Standard for Portable Fire Extinguishers, 2018 Edition, Chapter 6
Maximum floor area per unit of A: 1500 Sq.ft
Maximum floor area per extinguisher: 11,250 sq.ft
Maximum travel distance to extinguisher: 75 ft
Lock Box | Lockbox requirements | Link: https://www.calgary.ca/CSPS/Fire/Pages/Fire-codes/Lock-boxes.aspx
A lockbox provides emergency responders quick access to a building. They must contain all keys or devices required to access the building and the Fire/Life safety systems. All keys and devices must be attached to a key ring and their use indicated by an attached tag.
Lockboxes need to be installed on the exterior wall of the building within close proximity to the principal entrance.
Types of lockboxes
All buildings that require a lockbox must install one of two City of Calgary-approved products:
Trac-Vault
Trac-Tube
These approved boxes provide increased security and other benefits.
Buildings that require lockboxes
A lockbox needs to be installed on a building with any of the following:
A fire alarm system where
it's control features, including emergency voice communication systems, are located behind a locked pane.
manually operated devices require a key or device to be reset.
the electrical circuit breaker is located within a locked panel or room.
An automatic sprinkler system where the main control valve is locked in the open position or if it's located within a locked room or enclosure.
Standpipe and water supply connections are in a locked room or area such as a roof
A key operated elevator control feature that permits exclusive use of elevators to fire fighting personnel or that will switch selected elevators to operate on emergency power.
Stairway doors that have been locked on the stairway side.
Roof access doors that are locked.
Eye wash | In general, the ANSI standard provides that emergency equipment be installed within 10 seconds walking time from the location of a hazard (approximately 55 feet) (Appendix B5). The equipment must be installed on the same level as the hazard (i.e. accessing the equipment should not require going up or down stairs or ramps). The path of travel from the hazard to the equipment should be free of obstructions and as straight as possible. However, there are certain circumstances where these guidelines may not be adequate. Previous versions of the standard expressly provided that, where workers are handling particularly strong acids, caustics or other materials where the consequences of a spill would be very serious, emergency equipment should be installed immediately adjacent to the hazard. Although Appendix B5 of the 2014 standard briefly reviews the proper location of emergency equipment under such scenarios, we still believe the previous versions of the standard to be correct. Laboratory environments may also require special consideration. It has been common in many laboratory buildings to install emergency equipment in a corridor or hallway outside of the lab room. Since a door is considered an obstruction, this violates the provisions of the standard. For laboratory environments, we recommend installing (i) recessed laboratory eyewash/shower cabinets inside the lab room and (ii) dual purpose eyewash/drench hose units at lab sinks (see page 8). The recessed cabinet units are a space saving design that satisfy the standard’s requirements for both a shower and an eye/face wash, and are wheelchair accessible, while the eyewash/drench hoses provide immediate protection for the eyes, face or body when a spill involves a relatively small amount of hazardous material. | ANSI / ISEA Z358.1-2014
Codes for Maintenance & Inspection for Life Safety Equipment:
Equipment | Code | Details scope
Fire Alarm System | CAN-ULC-S537: Standard for Verification of Fire Alarm System / CAN-ULC-S536: Inspection and Testing of Fire Alarm Systems / National Fire Code - AB 2019 | Checklist in CAN ULC S537 Standard for Verification of Fire Alarm Systems & CAN/ULC-S536-13 Standard for Inspection and Testing of Fire Alarm Systems
Fire Sprinkler System | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 5 - Sprinkler System
NFPA 25\Chapter 13 - Common Components and Valves
Fire Standbypipes and Hose System | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 6 - Standpipe and Hose Systems
Automatic External Defibrillator | AED Management (City of Calgary) | AED Management Guide
Clean Agent Suppression | NFPA 2001: Standard on Clean Agent Fire Extinguishing Systems | NFPA 2001\Chapter 8 Inspection, Servicing, Testing, Maintenance
Gas Detector | NFPA 72 National Fire Alarm and Signaling Code | NFPA 72\Chapter 14 Inspection, Testing, and Maintenance
Carbon-monoxide-safety
NH3 Ammonia Detection System | CSA B52-05 Mechanical Refrigeration Code | B52 Mechanical Refrigeration Code - 2005, Section 8 Maintenance of Systems
Electromagnetic locks / Door hold-open device | National Building Code - AB 2019 (Ref: 14-BCV-011 / 14-FCV-012) | 14-BCV-011-14-FCV-012 Door Release Hardware
Elevators Recalls (Include in Quarterly Elevator Inspection by Contractor) | National Fire Code - AB 2019 (Section 7.2.2) & Elevating Device Code Regulation AR 62-2009 | National Fire Code of Canada - Alberta Edition 2019
Elevator Recall 2009_062
Emergency Generator | CSA-C282, Emergency Electric Power Supply for Buildings | CSA 282-15 Emergency Generator
Emergency Lighting | CSA-C22.2 no.141, Emergency Lighting / National Building Code - AB 2019 / National Fire Code - AB 2019 | NFC 2019 AB Section 6.5
Fire Dampers & Shutters | National Fire Code - AB 2019 / NFPA-80: Fire Doors and Other Opening Protectives | NFC 2019 Section 6.5 &NFPA 80\Chapter 19 Installation, Testing, and Maintenance of Fire Dampers
Fire Extinguishers | NFPA 10: Standard for Portable Fire Extinguisher | NFPA 10\Chapter 7 Inspection, Maintenance, and Recharging
Fire Hydrant | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 7 - Private Fire Service Mains
Grease Hood Fire Suppression | NFPA 17 Standard for Dry Chemical Extinguishing Systems, 2017 Edition, NFPA 17A Standard for Wet Chemical Extinguishing Systems, 2017 Edition & NFPA 96 Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations, 2017 Edition
Lockboxes | Fire Department - City of Calgary
Fire Pumps | NFPA 25: Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems | NFPA 25\Chapter 8 - Fire Pumps
Kitchen fire suppression (Ventilation Hood) | NFPA-17, 17A (Standard for Dry & Wet Chemical Extinguishing Systems) & 96 (Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations) | NFPA 72\Chapter 14 Inspection, Testing, and Maintenance
NFPA_Exhaust Hood Fire Suppression
Eye wash | ANSI / ISEA Z358.1-2014 Emergency Eye Wash & Shower Technology | ANSI / ISEA Z358.1-2014 Compliance Checklist

## FSHS-A-01
FSHS-A-01 | ANNUAL FIRE STANDPIPE AND HOSE SYSTEM INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Refer NFPA 25 Standard - Chapter 6 requirement for inspection
30 | ***Hose connection conditions***
40 | Valve cap(s) missing or damaged
50 | Fire hose connection damaged
60 | Valve handles missing or damaged
70 | Cap gaskets missing or deteriorated
80 | Valve leaking
90 | Visible and physical obstructions to hose connections
100 | Pressure restricting device missing
110 | Manual, semiautomatic, or dry standpipe valve does not operate smoothly
120 | Valve threads damaged
130 | **Piping**
140 | Any damaged piping and control valve?
150 | Missing pipe support device?
160 | Any damaged supervisory initiating device
170 | **Hose**
180 | Mildew, cuts, abrasions, and deterioration
190 | Couplings hose threads damaged
200 | Gaskets missing or deteriorated
210 | Incompatible threads on coupling
220 | Hose not connected to hose rack nipple or valve
230 | Hose test outdated
240 | ***Hose nozzle***
250 | Hose nozzle missing
260 | Gasket missing or deteriorated
270 | Any Obstructions
280 | Does not operate smoothly
290 | ***Hose Storage Device***
300 | Difficult to operate
310 | Any damaged
320 | Visible or physical obstruction
330 | Hose improperly racked or rolled
340 | Nozzle clip not in place and nozzle not correctly contained
350 | Hose rack enclosed in cabinet not swinging out at least 90 degrees
360 | ***Cabinet***
370 | Overall for corroded or damaged parts
380 | Difficult to open
390 | Cabinet door not opening fully
400 | Door glazing cracked or broken
410 | Lock on break glass–type cabinet not functioning properly
420 | Glass break device missing or not attached
430 | Not properly identified as containing fire equipment
440 | Visible or physical obstructions
450 | All valves, hose, nozzles, fire extinguishers, and so forth, easily accessible
455 | If fire extinguisher is in the cabinet, requires annual inspection at same time
460 | **Testing**
470 | Carry out hydrostatic, flow and hose test in every 5 years (if applicable)
480 | Conduct test for associated valves and components as per NFPA 25-Ch.13 (If app)
490 | Findings Reported To Maintenance Supervisor

## LS-FH-Q
LS-FH-Q | QUARTERLY PRIVATE FIRE HYDRANT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Locate hydrant shut off valve.
20 | Check for leaks in outlets or top of hydrant.
30 | Confirm hydrant is secured in the ground and all the bolts are in place.
40 | Inspect outer shell and flange for cracks & confirm hydrant is shut down.
50 | Inspect operating nut, threads, outlets & stem to insure all in good condition.
60 | Ensure availability of operating wrench.
70 | Findings reported to Maintenance Supervisor

## FH-A-01
FH-A-01 | ANNUAL PRIVATE FIRE HYDRANT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Refer to Code NFPA 25 - 2017, Chapter 7 for Annual Inspection
30 | Exposed piping shall be inspected annually
40 | Piping shall be inspected for the following conditions:
50 | (1) Leaks
60 | (2) Physical damage
70 | (3) Corrosion
80 | (4) Restraint methods
90 | ***Dry barrel and wall hydrants***
100 | It shall be inspected annually & after each operation for following conditions
110 | (1) Inaccessibility
120 | (2) Presence of water or ice in the barrel
130 | (3) Improper drainage from barrel
140 | (4) Leaks in outlets or at top of hydrant
150 | (5) Cracks in hydrant barrel
160 | (6) Tightness of outlet caps
170 | (7) Worn outlet threads
180 | (8) Worn hydrant operating nut
190 | (9) Availability of operating wrench
200 | ***Wet barrel hydrants***
210 | It shall be inspected annually & after each operation for following conditions
220 | (1) Inaccessibility
230 | (2) Leaks in outlets or at top of hydrant
240 | (3) Cracks in hydrant barrel
250 | (4) Tightness of outlet caps
260 | (5) Worn outlet threads
270 | (6) Worn hydrant operating nut
280 | (7) Availability of operating wrench
290 | Monitor nozzles shall be inspected for the following conditions:
300 | (1) Leakage
310 | (2) Physical damage
320 | (3) Corrosion
330 | Hose houses shall be inspected for the following conditions:
340 | (1) Inaccessibility
350 | (2) Physical damage
360 | (3) Missing equipment
370 | ***Flow Test***
380 | Hydrants shall be tested annually to ensure proper functioning.
390 | Each hydrant shall be opened fully & water flowed until all material cleared
400 | Flow shall be maintained for not less than 1 minute.
410 | Dry barrel and wall hydrants shall be observed for proper drainage from barrel
420 | Full drainage shall take no longer than 60 minutes.
430 | Where soil condition that the hydrant barrel does not drain within 60 minutes,
440 | If groundwater level is above hydrant drain, the hydrant drain shall be plugged
450 | and the water in the barrel shall be pumped out.
460 | Dry barrel hydrants before freezing weather and that have plugged drains
470 | it shall be identified clearly as needing pumping after operation.
480 | ***Others***
490 | All monitor nozzles shall be oscillated and moved throughout their full range
500 | Monitor nozzles shall be lubricated annually to ensure proper condition
510 | Hydrant lubricated annually to ensure that all stems, caps, plugs, and threads
520 | Hydrants shall be kept free of snow, ice, or other materials
530 | and protected against mechanical damage so that free access is ensured.
540 | Ensure submission of Inspection report from the vendor
550 | Follow up with vendor to rectify the defects or damages at once (if app)
560 | Findings reported to Facility Maintenance Coordinator
570 | Above task plan is the minimum requirement to follow
580 | Contractor is responsible to comply with all update and applicable codes as req

## FH-S-02
FH-S-02 | SEMI-ANNUAL PRIVATE FIRE HYDRANT INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment completed?
20 | Refer to Code NFPA 25 - 2017, Chapter 7 for Semi-Annual Inspection
30 | Hydrant shall be inspected for the following conditions:
40 | (1) Leaks
50 | (2) Physical damage
60 | (3) Corrosion
70 | Confirm hydrant is secured in the ground and all the bolts are in place.
80 | Visually locate hydrant shut off valve.
90 | Ensure hydrant is free for accessible and availability of operating wrench
100 | Inspect monitor nozzles for any inaccessibility, damages and missing equipment
110 | Inspect outer shell and flange for cracks & confirm hydrant is shut down.
120 | Remove the 125mm-steamer or one 65mm port cap.
130 | Listen on top nut with geophones or stethoscope for any leaks.
140 | Check hydrant barrel for water w/ rope/weight. Pump if hydrant barrel is wet.
150 | Replace all port caps and tighten.
160 | Monitor nozzles shall be inspected for the following conditions:
170 | (1) Leakage
180 | (2) Physical damage
190 | (3) Corrosion
200 | Hose houses shall be inspected for the following conditions:
210 | (1) Inaccessibility
220 | (2) Physical damage
230 | (3) Missing equipment
240 | If groundwater level is above hydrant drain, the hydrant drain shall be plugged
250 | and the water in the barrel shall be pumped out.
260 | Dry barrel hydrants before freezing weather and that have plugged drains
270 | it shall be identified clearly as needing pumping after operation.
280 | ***Others***
290 | Hydrants shall be kept free of snow, ice, or other materials
300 | and protected against mechanical damage so that free access is ensured.
310 | Ensure submission of Inspection report from the vendor
320 | Follow up with vendor to rectify the defects or damages at once (if app)
330 | Findings reported to Facility Maintenance Coordinator
340 | Above task plan is the minimum requirement to follow
350 | Contractor is responsible to comply with all update and applicable codes as req

## LS-FH-A
LS-FH-A | ANNUALLY PRIVTE FIRE HYDRANT INSPECTION
Sequence | Description
5 | Pre Job Hazard Assessment completed?
10 | Refer NFPA 25 Standard - Chapter 7 requirement for inspection
20 | ***Exposed Piping***
30 | Leaks
40 | Physical damage
50 | Corrosion
60 | Resttaint methods
70 | ***Underground Piping***
80 | Mainline strainers shall be inspected and cleaned after each system flow exceeding that of a nominal 2 in. (50 mm) orifice.
90 | Mainline strainers shall be removed and inspected for plugging, fouling, and damaged and corroded parts.
100 | ***Dry barrel and wall hydrants*** | 7.2.2.4
110 | Inaccessibility
120 | Presence of water or ice in the barrel (could indicate a faulty drain, a leaky hydrant valve, or high groundwater table)
130 | Improper drainage from barrel
140 | Leaks in outlets or at top of hydrant
150 | Cracks in hydrant barrel
160 | Tightness of outlet caps
170 | Worn outlet threads
180 | Worn hydrant operating nut
190 | Availability of operating wrench
200 | Corrective action shall be taken for any deficiencies is noted
205 | ***Wet barrel hydrants*** | 7.2.2.5
210 | Inaccessibility
220 | Leaks in outlets or at top of hydrant
230 | Cracks in hydrant barrel
240 | Tightness of outlet caps
250 | Worn outlet threads
260 | Worn hydrant operating nut
270 | Availability of operating wrench
280 | ***Hydrant*** | 7.3.2
290 | Each hydrant shall be opened fully and water flowed until all foreign material has cleared.
300 | Flow shall be maintained for not less than 1 minute.
310 | Full drainage shall take no longer than 60 minutes.
320 | Any improper drainage from barrel observed
330 | If yes, the water in the barrel shall be pumped out
340 | Hydrants shall be lubricated to ensure that all stems, caps, plugs, and threads are in proper operating condition
350 | Hydrants shall be kept free of snow, ice, or other materials and protected against mechanical damage so that free access is ensured.
360 | Monitor nozzles shall be lubricated to ensure proper operating condition. | 7.3.3.2
370 | Lubricate hydrant to ensure all stems, caps, plugs in proper operating condition | 7.4.2.1
380 | Findings reported to Maintenance Supervisor

## FE-M-01
FE-M-01 | MONTHLY FIRE EXTINGUISHER INSPECTION
Sequence | Description | Existing task plan in EAM
10 | Pre Job Hazard Assessment Completed? | 10 | Ensure Fire Extinguisher Is In Designated Place
20 | Refer NFPA 10 Standard - Chapter 7 requirement for inspection | 20 | Ensure There Are No Obstructions To Access Or Visibility
30 | Ensure Fire Extinguisher Is In Designated Place | 30 | Ensure Pressure Gauge Reading Or Indicator Is In The Operable Range Or Position
40 | Ensure There Are No Obstructions To Access Or Visibility | 40 | Ensure Fire Extinguisher Is Full By Lifting Or Hefting
50 | Ensure Pressure Gauge Reading Or Indicator Is In The Operable Range Or Position | 50 | Ensure Fire Extinguisher Is Not Exposed To Abnormal Temp Or Corrosive Atmosphere
60 | Ensure Fire Extinguisher Is Full By Lifting Or Hefting | 60 | Ensure Operating Instructions On Nameplate Are Legible And Face Outward
70 | Ensure Fire Extinguisher Is Not Exposed To Abnormal Temp Or Corrosive Atmosphere | 70 | Check For Broken Or Missing Safety Seals And Tamper Indicators
80 | Ensure Operating Instructions On Nameplate Are Legible And Face Outward | 80 | Examine For Obvious Physical Damage, Corrosion, Leakage Or Clogged Nozzle
90 | Check For Broken Or Missing Safety Seals And Tamper Indicators | 90 | Sign The Monthly Inspection Tag Attached To The Device.
100 | Examine For Obvious Physical Damage, Corrosion, Leakage Or Clogged Nozzle | 100 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
110 | Sign The Monthly Inspection Tag Attached To The Device. | 110 | Pre Job Hazard Assessment Completed?
120 | Findings Reported To Maintenance Supervisor
Existing task plan in EAM
|  | 10 | Inspect, Test & Recharge All Fire Extinguishers In Building
|  | 20 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
|  | 30 | Pre Job Hazard Assessment Completed?

## LS-FI-PU-W
LS-FI-PU-W | WEEKLY FIRE PUMP INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer NFPA 25 Standard - Chapter 8 (8.2.2 & 8.3.2.9) requirement for inspection
30 | **Pump house condition***
40 | Not less than 4.0 Deg.C for electric motor or diesel engine pump with engine heaters
50 | Not less than 21.0 Deg.C with disel pump without enginer heaters
60 | Ventilation louvres are free to operate
70 | Excessive water does not collect on floor
80 | Coupling guard in place
90 | ***Pump system condition***
100 | Pump suction and discharge and bypass valve are fully open
110 | Piping is free of leaks
120 | Suction line pressure gauge reading is within acceptable range.
130 | System line pressure gauge reading is within acceptable range.
140 | Suction reservoir has the required water level.
150 | Wet pit suction screens are unobstructed and in place.
160 | Waterflow test valves are in the closed position,
170 | The hose connection valve is closed, and the line to test valves is free of water.
180 | Record the pump starting pressure from pressure switch under running | 8.3.2.9
190 | Recod the system suction and discharge gauge readings (PSI) | 8.3.2.9
200 | Inspect the pump packing glands for slight discharge | 8.3.2.9
210 | Adjust glands nuts if needed | 8.3.2.9
220 | Inspect for abnormal noise or vibration | 8.3.2.9
230 | Inspect packing box, bearings or pump casing for overheating | 8.3.2.9
240 | Record pressure switch reading and compare to the pump discharge gauge | 8.3.2.9
250 | Check the circulation relief valve for operation to discharge water | 8.3.2.9
260 | ***Electrical system conditions***
270 | Controller pilot light (power on) is illuminated.
280 | Transfer switch normal pilot light is illuminated.
290 | Isolating switch is closed — standby (emergency) source.
300 | Reverse phase alarm pilot light is off, or normal phase rotation pilot light is on.
310 | Oil level in vertical motor sight glass is within acceptable range.
320 | Power to pressure maintenance (jockey) pump is provided.
330 | Observe the time for motor to accelerate to full speed | 8.3.2.9
340 | Record the time pump runs after starting | 8.3.2.9
350 | ***Diesel engine system conditions***(If applicable)
360 | Fuel tank is at least two-thirds full.
370 | Controller selector switch is in auto position.
380 | Batteries’ voltage readings are within acceptable range.
390 | Batteries’ charging current readings are within acceptable range.
400 | Batteries’ pilot lights are on or battery failure pilot lights are off.
410 | All alarm pilot lights are off.
420 | Engine running time meter is reading.
430 | Oil level in right angle gear drive is within acceptable range.
440 | Crankcase oil level is within acceptable range.
450 | Cooling water level is within acceptable range.
460 | Electrolyte level in batteries is within acceptable range.
470 | Battery terminals are free from corrosion.
480 | Water-jacket heater is operating.
490 | Conduct no-low test for diesel enginer-driven pump (if applicable)
500 | Observe the time for engine to crank | 8.3.2.9
510 | Observe the tie for engine to reach running speed | 8.3.2.9
520 | Observe the engine oil pressure gauge, speed indicator | 8.3.2.9
530 | Record any abnormailities | 8.3.2.9
540 | Inspect the heat exchanger for cooling waterflow | 8.3.2.9
Existing tasks in EAM (PU-I-03)
Sequence | Description
10 | Under No Circumstances Will The Fire Panel Be Left Unattended While Bypassed
20 | System Pressure
30 | City Pressure
40 | Open Test Valve Slowly
50 | Jockey Pump Cut-In Pressure
60 | Turn Off Jockey Pump
70 | Fire Pump Cut-In Pressure
80 | Close Test Valve
90 | Allow Fire Pump To Run 10 Minutes (On Timer)
100 | Turn Jockey Pump Back To Auto
110 | Jockey Pump To Run 2 Minutes (On Timer)
120 | Verify Relief Valves Open (2)
130 | Verify Fire Pump Run Status On Fire Panel-Check Bearing Packing
140 | Verify Fire Pump Run Status On Fire Panel-System Pressure (During Test)
150 | Verify Fire Pump Run Status On Fire Panel-Return Jockey Pump To Auto
160 | System Pressure (After Test)
170 | City Pressure (After Test)
180 | Reset Fire Panel And Turn Off Bypasses
190 | Bocc To Go Back Online: Electrician To Turn On/Off Bypasses On Fire Alarm Panel.
200 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
210 | Pre Job Hazard Assessment Completed?

## VHD-S-01
VHD-S-01 | SEMI ANNUALLY KITCHEN VENTILATION HOOD CLEAN UP AND FIRE SUPPRESSION INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refers to NFPA-17, 17A (Standard for Dry & Wet Chemical Extinguishing Systems) for inspection
30 | & NFPA 96 (Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations)
40 | Remove Hardened Grease from Ductwork
50 | Remove fan and spray both the top and bottom of the fan with cleaning chemical
60 | Pressure wash entire system
70 | Replace Filters and Polish Hood
80 | Clean up Kitchen
90 | Apply Certification Sticker
100 | Extinguishing system nozzles are located directly above grease producing equipment
110 | The manual actuators are unobstructed
120 | The tamper indicators and seals are intact
130 | The maintenance tag or certificate is in place
140 | No obvious physical damage or condition exists that might prevent operation
150 | The pressure gauge(s) are in operable range
160 | The nozzle blow-off caps are intact and undamaged
170 | Neither protected equipment nor hazard had been replaced, modified or relocated
180 | Remove grease from exhaust systems serving solid fuel cooking operation
190 | Check electrostatic precipitator on recirculating system
200 | Gas and electric power shutoff are operational
210 | Water-wash hood cleaning systems are operational and protected by sprinkler system
220 | Check recirculating system operation and safety interlocks
230 | Manual release stations are operational and send a signal to the building fire alarm control panel
240 | Automatic release devices are operational and send a signal to the building fire alarm control panel
250 | Water flow, valve tamper, and low water pressure cut-offs are operational
260 | Verify agent distribution piping is not obstructed
270 | Replace fixed temperature sensing elements of the fusible alloy type if needed
280 | Clean fixed temperature sensing elements other than the fusible metal alloy type
290 | Examine detectors, expellant gas container, agent containers and auxiliary equipment
300 | Hydrostatic pressure test on wet and dry chemical extinguishing systems (Every 12 years)
310 | Findings Reported To Maintenance Supervisor
Existing tasks in EAM (VHD-01)
Sequence | Description
10 | Clean Grease Baffle Filters
20 | Remove Hardened Grease from Ductwork
30 | Remove fan and spray both the top and bottom of the fan with cleaning chemical
40 | Clean Exhaust Fan
50 | Pressure wash entire system
60 | Replace Filters and Polish Hood
70 | Clean up Kitchen
80 | Apply Certification Sticker

## LB-01
LS-LB-S | SEMI ANNUALLY LOCK BOX INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Check Keys In Lock Boxes To Ensure That They Are Correct For The Specific Site
30 | Make Sure Keys Will Allow Emergency Responders Access Into The Facility

## EG-W-01
EG-W-01 | WEEKLY EMERGENCY GENERATOR INSPECTION
Sequence | Description
10 | Pre Job Hazard Assessment Completed?
20 | Refer to CSA C282-15 For Emergency Generator Weekly Inspection
30 | ***Consumables***
40 | Inspect auxiliary supply tank fuel level (gas pressure) if applicable
50 | Inspect main tank level (gas pressure) if applicable.
60 | Minimum 2 hours fuel supply required
70 | Inspect lubricating oil level.
80 | Inspect engine coolant level.
90 | Inspect engine, generator, fuel tank(s), and cooling systems for leakage.
100 | Inspect for proper operation of fuel transfer pump (if applicable).
110 | Inspect fuel filter for contamination if filter is equipped with a transparent b
120 | ***Starter system***
130 | Inspect electric starter for cleanliness, mounting, and terminal security.
140 | For Air starter:
150 | Inspect air tanks for pressure.
160 | Inspect valves for leakage.
170 | Test auxiliary engine and compressor for proper operation.
180 | Bleed off any condensation.
190 | ***Batteries and charging equipment***
200 | Inspect all battery cells for correct electrolyte fill level (Lead-acid battery)
210 | Test battery cells for correct electrolyte specific gravity (Lead-acid battery)
220 | Inspect electrical connections for tightness and evidence of corrosion.
230 | Inspect battery for cleanliness and dryness between terminals.
240 | Inspect charger electrical connections for cleanliness and tightness.
250 | ***Engine***
260 | Test lubricant and/or coolant heaters for proper operation.
270 | Inspect governor control linkages and oil level (if applicable).
280 | Inspect fuel pump oil sump (if applicable).
290 | Inspect fan belts for correct tension and wear.
300 | ***Control panel***
310 | Inspect control panel covers for security.
320 | Test annunciator lamps to confirm that they are operational.
330 | Inspect control panel settings (ensure the unit is ready for automatic start-up)
340 | Test remote visual and audible trouble signals at the building fire alarm panel.
350 | ***Others***
360 | Inspect air control louvre settings to ensure proper operation
370 | Test emergency lighting unit
380 | Verify whether room temperature is above 10 Deg.C
390 | Inspect generator and transfer switch room(s) for cleanliness and accessibility
400 | Correct all defects found during inspections and tests.
410 | Record all inspections, tests, and corrective actions in the log
420 | Findings Reported To Maintenance Supervisor
Existing task in EAM
10 | Refer To Canadian Standards Association (Csa) For Emer Generator Weekly Insp.
20 | Csa Standard No. C282-09 -- Emergency Electrical Power Supply For Buildings
30 | Transfer Switch(S) Into Auto
40 | Gen Control In Auto
50 | Diesel Fuel Level (Daytank)
60 | Diesel Fuel Level (Undrgndtank)
70 | Current Fuel Level In Main Tank
80 | Fuel Filter/Water Separator
90 | Coolant Heater Operation
100 | Gas Line Condition
110 | Engine Oil Level
120 | Air Filter Condition
130 | Belt Condition
140 | Coolant Level / Sg (Monthly)
150 | Battery Level / Sg (Monthly)
160 | Starter, Batt. Chgr. Connections
170 | Battery Charger Voltage
180 | Battery Charger Amps
190 | Battery Volts (Actual, Monthly)
200 | Isolation Breakers Closed
210 | Emergency Lighting Operation
220 | Lamp Test (Trans & Gen)
230 | Louver(S) Position
240 | Check For Leaks
250 | Spill Kit Available
260 | Room/Area Cleanliness
270 | Operator / Date
280 | Findings Reported To Facility Supervisor And Facility Operations Coordinator
290 | Pre Job Hazard Assessment Completed?